## LOG
Date | Name | Sheet Name | Cells | Comments
2020-08-13 | Dmytro Romanchenko |  |  | Composed this file (combined VT and SubRes info) based on the DataCenters representation in the TIMES-DK model

## Processes_Commodities
Formated from the TIMES-DK model files
~FI_Process
Sets | Region | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
*Process Set Membership | Region Name | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
DMD |  | LDCFC | Large Data Centers Facility - Central | PJ | MW
|  | LDCFD | Large Data Centers Facility - Decentral | PJ | MW
PRE |  | FT-LDCELC | Fuel Technology - Large Data Centers Electricity | PJ | Pja | DAYNITE |  |  | why DAYTIME slicing for FT processes?? It is only assigning electricity to it's later demadn categoty, isn't it?
|  | FT-LDCCSELC | Fuel Technology - Large Data Centers Cooling System Electricity | PJ | Pja | DAYNITE
|  | EXHLDCHXC | Excess Heat Large data Centers - Heat Exchanger - Centralised | PJ | MW | DAYNITE |  | YES
|  | EXHLDCHXD | Excess Heat Large data Centers - Heat Exchanger - Decentralised | PJ | MW | DAYNITE |  | YES
|  | EXHLDCHPC | Excess Heat Large data Centers - Heat Pump - Centralised | PJ | MW | DAYNITE |  | YES
|  | EXHLDCHPD | Excess Heat Large data Centers - Heat Pump - Decentralised | PJ | MW | DAYNITE |  | YES
~FI_Comm
CSet | Region | CommName | CommDesc | Unit | LimType | CTSLvl | PeakTS | Ctype
*Commodity Set Membership | Region Name | Commodity Name | Commodity Description | Unit | Sense of the Balance EQN. | Timeslice Level | Peak Monitoring | Electricity Indicator
DEM |  | ELDCC | Electricity Large Data Centers Demand - Central | PJ |  | DAYNITE
|  | ELDCD | Electricity Large Data Centers Demand - Decentral | PJ |  | DAYNITE
NRG |  | LDCELC | Electricity used by Large Data Centers - operation | PJ |  | DAYNITE |  | ELC
|  | LDCCSELC | Electricity used by Large Data Centers - cooling | PJ |  | DAYNITE |  | ELC
|  | LDCLTHC | Large Data Centers - Low Temperature Heat - Central | PJ
|  | LDCLTHD | Large Data Centers - Low Temperature Heat - Decentral | PJ
|  | HETCLDCEH | Large Data Centers Excess heat (20 degrees) to HP - Central | PJ
|  | HETDLDCEH | Large Data Centers Excess heat (20 degrees) to HP - Decentral | PJ
do we need to indicate all the regions here? Or are all of those processes and commodities applied to all of the regions if the "Region" cells are blank

## IND_DataCenters
Formated from the TIMES-DK model files
~FI_T
TechName | *TechDesc | Region | Comm-IN | Comm-IN-A | Comm-OUT | Comm-OUT-A | Year | CURR | START | EFF | Share-I~2015 | Share-I~2020 | Share-I~2030 | Share-I~2050 | Share-I~0 | INVCOST | FIXOM | VAROM | AFA | PRC_CAPACT | VDA_FLOP | LIFE | ILED | PEAK
*Technology Name | Technology Description | Region Name | Input Commodity | Auxiliary Input Commodity | Output Commodity | Auxiliary Output Commodity | Year | Currency | Starting Year | Efficiency |  |  |  |  | Interpolation rule for Share | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Annual Availability Factor | Capacity to Activity Factor | Process Input/Output tied to activity | Lifetime of Process | Construction time | Fraction of capacity in peak eqn
*Unit | [15 empty] | MKr/MW | MKr/MW | MKr/PJ |  |  | PJ per PJ activity | Years | Years
FT-LDCELC | Fuel Technology - Large Data Centers Electricity |  | INDELC |  | LDCELC |  |  |  |  | 1 | [11 empty] | 100
FT-LDCCSELC | Fuel Technology - Large Data Centers Cooling System Electricity |  | INDELC |  | LDCCSELC |  |  |  |  | 1 | [11 empty] | 100
LDCFC | Large Data Centers Facility - Central |  | LDCELC |  | ELDCC |  |  |  |  | 1 | [8 empty] | 1 | 0.031536 |  | 50
|  |  |  | LDCCSELC | [16 empty] | 0.12443
[6 empty] | LDCLTHC | [14 empty] | 0.58155
LDCFD | Large Data Centers Facility - Decentral |  | LDCELC |  | ELDCD |  |  |  |  | 1 | [8 empty] | 1 | 0.031536 |  | 50
|  |  |  | LDCCSELC | [16 empty] | 0.12443
[6 empty] | LDCLTHD | [14 empty] | 0.58155
EXHLDCHXC | Excess Heat Large data Centers - Heat Exchanger - Centralised |  | LDCLTHC |  | HETCLDCEH |  | 2015 | MKr12 | 2017 | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
[7 empty] | 2020 | MKr12 |  | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
[7 empty] | 2030 | MKr12 |  | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
[7 empty] | 2050 | MKr12 |  | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
EXHLDCHXD | Excess Heat Large data Centers - Heat Exchanger - Decentralised |  | LDCLTHD |  | HETDLDCEH |  | 2015 | MKr12 | 2017 | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
[7 empty] | 2020 | MKr12 |  | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
[7 empty] | 2030 | MKr12 |  | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
[7 empty] | 2050 | MKr12 |  | 1 | [5 empty] | 0.5215 | 0.03725 | 0 | 1 | 0.031536 |  | 20 | 0.5 | 1
EXHLDCHPC | Excess Heat Large data Centers - Heat Pump - Centralised |  | HETCLDCEH |  | HETC |  | 2015 | MKr15 | 2017 | 1 | 0.78575 |  |  |  | 5 | 5.215 | 0.0149 | 4.1389 | 0.99038 | 0.031536 |  | 25 | 0.5 | 1
|  |  | ELCC | [7 empty] | 0.21425 |  |  |  | 5
|  |  | HETCLDCEH |  |  |  | 2020 | MKr15 |  | 1 |  | 0.8495 |  |  | 5 | 4.9021 | 0.0149 | 3.725
|  |  | ELCC | [8 empty] | 0.1505 |  |  | 5
|  |  | HETCLDCEH |  |  |  | 2030 | MKr15 |  | 1 |  |  | 0.8495 |  | 5 | 4.4119 | 0.0149 | 3.5181
|  |  | ELCC | [9 empty] | 0.1505 |  | 5
|  |  | HETCLDCEH |  |  |  | 2050 | MKr15 |  | 1 |  |  |  | 0.9049 | 5 | 3.9707 | 0.0149 | 3.3111
|  |  | ELCC | [10 empty] | 0.095103 | 5
EXHLDCHPD | Excess Heat Large data Centers - Heat Pump - Decentralised |  | HETDLDCEH |  | HETD |  | 2015 | MKr15 | 2017 | 1 | 0.80527 |  |  |  | 5 | 5.215 | 0.0149 | 4.1389 | 0.99038 | 0.031536 |  | 25 | 0.5 | 1
|  |  | ELCC | [7 empty] | 0.19473 |  |  |  | 5
|  |  | HETDLDCEH |  |  |  | 2020 | MKr15 |  | 1 |  | 0.8495 |  |  | 5 | 4.9021 | 0.0149 | 3.725
|  |  | ELCC | [8 empty] | 0.1505 |  |  | 5
|  |  | HETDLDCEH |  |  |  | 2030 | MKr15 |  | 1 |  |  | 0.8495 |  | 5 | 4.4119 | 0.0149 | 3.5181
|  |  | ELCC | [9 empty] | 0.1505 |  | 5
|  |  | HETDLDCEH |  |  |  | 2050 | MKr15 |  | 1 |  |  |  | 0.9049 | 5 | 3.9707 | 0.0149 | 3.3111
|  |  | ELCC | [10 empty] | 0.095103 | 5
|  | do we need to indicate all the regions here? Or are all of those processes and commodities applied to all of the regions if the "Region" cells are blank | [18 empty] | what do these numbers mean?
Taken from the TIMES_DK model.
|  | RES explanation (example) | [10 empty] | Efficiency corrections of the Datacenters
[13 empty] | DKE | DKE | DKW | DKW
| electricity | ELCC | FT-LDCELC | LDCELC | LDCFC | ELDCC | [6 empty] | Central | Decentral | Central | Decentral
|  | comodity | process | commodity | process | commodity | [5 empty] | 2015 | 4.6674 | 5.1352 | 5.6187 | 5.9558
[8 empty] | ELCC |  |  |  | 2020 | 6.6447 | 6.6447 | 6.6447 | 6.6447
| cooling/heating | ELCC | FT-LDCCSELC | LDCCSELC | LDCFC | LDCLTHC | EXHLDCHXC | HETCLDCEH | EXHLDCHPC | HETC |  | 2030 | 6.6447 | 6.6447 | 6.6447 | 6.6447
|  | comodity | process | commodity | process | commodity | process | commodity | process | commodity |  | 2050 | 10.5149 | 10.5149 | 10.5149 | 10.5149
Note on C4: With this character *, this column is ignored from VEDA. It is just useful for your information

## Demand
~FI_T
CommName | *Description | *Unit | DEMAND~DKE | DEMAND~DKW | DEMAND~SE1 | DEMAND~SE2 | DEMAND~SE3 | DEMAND~SE4 | DEMAND~NO1 | DEMAND~NO2 | DEMAND~FI1 | DEMAND~FI2 | DEMAND~ISL
ELDCC | Electricity Large Data Centers Demand - Central | PJ
ELDCD | Electricity Large Data Centers Demand - Decentral | PJ
Numers for the base year demand are to be found and added here, I assume
(could not find any numbers in the TIMES-DK files)

## HX_TechData
This entire sheet is kept unchanged from the TIMES-DK model
Comm | Year | EFF | *ELCC Input | *Minimum capacity | INVCOST | FIXOM | VAROM | CAP2ACT | AFA | Peak | LIFE
Degrees of waste heat |  |  | Electricity consumption | Minimum capacity for technology | Total cost of investment in new capacity | Annual fixed O&M cost | Annual variable O&M cost | Units of activity/unit of capacity | Annual availability/utilization factor | Fraction of capacity in peak equations | Technical life | Currency Conversion
|  |  |  | kW | MKr/MW | MKr/MW | MKr/PJ | Factor | Factor |  | Years | DKK/EU | 7.45
40 | 2015 | 1 |  | 250 | 0.5215 | 0.03725 | 0 | 0.031536 | 1 | 1 | 20
| 2020 | 1 |  | 250 | 0.5215 | 0.03725 | 0 |  |  |  | 20
| 2030 | 1 |  | 250 | 0.5215 | 0.03725 | 0 |  |  |  | 20
| 2050 | 1 |  | 250 | 0.5215 | 0.03725 | 0 |  |  |  | 20
Data for the danish energy agency 2017 technology catalog
Technology | District heating substation
Apartment complex, existing and new building
| 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
Heat production capacity for one unit (kW) | 250 | 250 | 250 | 250 | A
Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100
Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100
Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | B
Technical lifetime (years) | 20 | 20 | 20 | 20
Environment
SO2 (g per GJ fuel) | - | - | - | -
NOX (g per GJ fuel) | - | - | - | -
CH4 (g per GJ fuel) | - | - | - | -
N2O (g per GJ fuel) | - | - | - | -
Particles (g per GJ fuel) | - | - | - | -
Financial data
Specific investment (1000€/kW) | 0.07 | 0.07 | 0.07 | 0.07 | G | 2, 4
Specific investment (1000€/unit)
- hereof equipment (%) | 70 | 70 | 70 | 70
- hereof installation (%) | 30 | 30 | 30 | 30
Possible additional specific investment (1000€/unit) | 4 | 4 | 4 | 4 | D
Fixed O&M (€/unit/year) | 1250 | 1250 | 1250 | 1250 |  | 7
Variable O&M (€/GJ)
Note on J5: Iben Moll Rasmussen: What does this mean?
Note on J6: Mikkel Bosack Simonsen: asummed similar to ELC HP with ambient temperature
Note on K6: Mikkel Bosack Simonsen: asummed similar to ELC HP with ambient temperature
Note on L6: Mikkel Bosack Simonsen: asummed similar to ELC HP with ambient temperature

## HP_TechData
This entire sheet is kept unchanged from the TIMES-DK model
Comm | Year | *ELCC Input | *Minimum capacity | INVCOST | FIXOM | VAROM | CAP2ACT | AFA | Peak | LIFE | ILED
Degrees of Source Temperature |  | Electricity consumption | Minimum capacity for technology | Total cost of investment in new capacity | Annual fixed O&M cost | Annual variable O&M cost | Units of activity/unit of capacity | Annual availability/utilization factor | Fraction of capacity in peak equations | Technical life | Construction time | Currency Conversion
|  |  | MW | MKr/MW | MKr/MW | MKr/PJ | Factor | Factor |  | Years | Years | DKK/EU | 7.45
22.4659 | 2015 | 0.22727 | 4 | 5.215 | 0.0149 | 4.1389 | 0.031536 | 0.99038 | 1 | 25 | 0.5
| 2020 | 0.2 | 4 | 4.9021 | 0.0149 | 3.725
| 2030 | 0.16667 | 4 | 4.4119 | 0.0149 | 3.5181
| 2050 | 0.13514 | 4 | 3.9707 | 0.0149 | 3.3111
[14 empty] | T_source in [K] = | 301
[14 empty] | T_source out [K] = | 290
[14 empty] | T_lm, source [C] = | 22.4659
Data for the danish energy agency 2017 technology catalog
Technology | 40 Electrical compression heat pumps - district heating
| 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Heat generation capacity for one unit (MWheat) | 4 | 4 | 4 | 4 | 3 | 6 | 3 | 10 |  | 3
Total efficiency, net (%), name plate | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total eff., net (%), annual average, ambient heat source, no dev. in supply temp. | 350 | 360 | 380 | 410 | 350 | 380 | 350 | 450 | A, F, J, K | 4
Total eff., net (%), annual average, ambient heat source, reduced supply temp. | 350 | 400 | 480 | 600 | 350 | 450 | 350 | 700 | A, B, F, J | 3, 4
Total eff., net (%), annual average, waste heat 20° C, reduced supply temp. | 440 | 500 | 600 | 740 | 440 | 600 | 440 | 850 | A, B, F, J | 3, 4
Total eff., net (%), annual average, waste heat 40° C, reduced supply temp. | 700 | 900 | 1200 | 1800 | 700 | 1200 | 700 | 2000 | A, B, F, J | 3, 4
Electricity consumption for pumps etc. (% of heat gen) | 10 | 9 | 7 | 4 | 4 | 10 | 3 | 6 | I, M | 3
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | G | 3
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 | H | 3
Technical lifetime (years) | 25 | 25 | 25 | 25 | 15 | 30 | 15 | 30 |  | 3
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 | C
Space requirement (1000m2 per MWheat) | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.04 | 0.01 | 0.04 |  | 1
Regulation ability
Primary regulation (% per 30 seconds) | 10 | 10 | 10 | 10 | 10 | 25 | 10 | 30 | D | 3
Secondary regulation (% per minute) | 20 | 20 | 20 | 20 | 20 | 40 | 20 | 40 | D | 3
Minimum load (% of full load) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | D | 3
Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 3
Cold start-up time (hours) | 6 | 6 | 6 | 6 | 1 | 12 | 1 | 12 | E | 8,10
Environment
SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
Nominal investment (M€ per MWheat) | 0.7 | 0.658 | 0.5922 | 0.53298 | 0.5 | 1 | 0.5 | 1 | A, L
- of which equipment (%) | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
- of which installation (%) | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
Fixed O&M (€/MWheat/year) | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 3000 |  | 3
Variable O&M (€/MWhheat) | 8.4 | 8.2 | 8.8 | 8.2 | 4.3 | 9.1 | 6.5 | 11.9
- of which is electricity costs (€/MWhheat) | 6.4 | 6.4 | 7.1 | 6.6 | 2.8 | 7.1 | 5 | 9.9 | M
- of which is other O&M costs (€/MWhheat) | 2 | 1.8 | 1.7 | 1.6 | 1.5 | 2 | 1.5 | 2 | F | 3
Technology specific data
From Danish Energy Agency technology catalogue 2017
Heat Exchanger
Air from/to data center
Closed loop for source of HP
T_air,in = 31 C
T_air,out = 20 C
T_source,in = 28 C
T_source,out = 17 C
Assumed configuration: HX followed by heat pump

## COP DH_LDC
This entire sheet is kept unchanged from the TIMES-DK model
OBJECTID | forsytekst | CVR_number | Cen_Dec | DKE_DKW | Internt energitab | Supp_temp_summ | Ret_temp_summ | Supp_temp_wint | Ret_temp_wint | Cooling | Net_loss_perc
1 | AGERSTED VARMEVÆRK | 29189 | Decentral | DKW | [7 empty] | AFFALDVARME AARHUS |  | 75 | 46 | 81 | 42 | 27.491 | 21% | 1818.244 | 1 | The COP values for the excess heat heat pumps has been calculated using Carnot´s formula of efficiency, with assumptions showed in the table. Future Temperatures of DH grid, based on similar assumptions made by the Danish Energy agency, are used for calculatiung future COP values for HP | [14 empty] | The COP values for the excess heat heat pumps has been calculated using Lorentz formula of efficiency, with assumptions showed in the table. Future Temperatures of DH grid, based on similar assumptions made by the Danish Energy agency, are used for calculatiung future COP values for HP
2 | Allerød Kommune | 60183 | Decentral | DKE | [7 empty] | ALLINGÅBRO VARMEVÆRK A.M.B.A. |  | 75 | 37 | 83 | 37 |  | 27.87% | 11.67 | 2 |  |  | SPRING |  | SUMMER |  | AUTUMN |  | WINTER |  | Assumptions | [6 empty] | SPRING |  | SUMMER |  | AUTUMN |  | WINTER |  |  | Assumptions
3 | ALLINGÅBRO VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 75 | 37 | 83 | 37 | 0 | 27.87% | ALS FJERNVARME A.M.B.A. |  | 75 | 35 | 82 | 38 | 28.7788 | 15.25% | 9.0773 | 3 |  |  | Supp_temp_spr | Ret_temp_sspr | Supp_temp_summ | Ret_temp_summ | Supp_temp_aut | Ret_temp_aut | Supp_temp_wint | Ret_temp_wint |  | Avg. EH T |  | Avg. EH Delta_T | Outlet temp | °C |  | Supp_temp_spr | Ret_temp_sspr | Supp_temp_summ | Ret_temp_summ | Supp_temp_aut | Ret_temp_aut | Supp_temp_wint | Ret_temp_wint |  |  |  |  | Avg. EH T |  | Avg. EH Delta_T | Outlet temp |  |  |  | Tech catalogue Lorents efficiency calculation
4 | ALS FJERNVARME AMBA | 29189 | Decentral | DKW | 0% | 75 | 35 | 82 | 38 | 28.7788 | 15.25% | ANSAGER VARMEVÆRK A.M.B.A. | 2.685% | 76 | 38 | 76 | 34 | 41.4162 | 24.04% | 10.826 | 4 | Central | DKE | 81.85 | 48.9031 | 77.8353 | 49.1875 | 81.85 | 48.9031 | 85.8647 | 48.6188 | LTEH | 47 | °C | 5 | 10 | Central | DKE | 81.85 | 48.9031 | 77.8353 | 49.1875 | 81.85 | 48.9031 | 85.8647 | 48.6188 |  | LTEH | 37.5 | °C | 310.65 | °K | 5 | 288.15 | °K
5 | ANDELSSELSKABET MØLHOLM VARMEVÆRK | 29189 | Central | DKW | 0% | 63 | 63 | 73 | 73 | 20.7833 | 21.57% | ASSENS FJERNVARME - FYN | 0.7025% | 75 | 43 | 75 | 38 | 36.2183 | 24.02% | 66.662 | 5 | Central | DKW | 74.0862 | 41.0238 | 70.5659 | 42.5996 | 74.0862 | 41.0238 | 77.6066 | 39.448 | MTEH | 70 | °C | 10 | 10 | Central | DKW | 74.0862 | 41.0238 | 70.5659 | 42.5996 | 74.0862 | 41.0238 | 77.6066 | 39.448 |  | MTEH | 70 | °C | 343.15 | °K | 10 | 288.15 | °K |  | Tech | Year | COP mean | COP Low | COP High | DH T in | DH T out | Source, in | Source, out | luft | vand | Lorentz efficiency, mean | Lorentz efficiency, Low | Lorentz efficiency, High
6 | ANDELSSELSKABET MØLHOLM VARMEVÆRK | 29189 | Decentral | DKW | 0% | 63 | 63 | 73 | 73 | 20.7833 | 21.57% | ASAA FJERNVARME |  | 67 | 38 | 67 | 34 | 32.9449 | 25.54% | 9.457 | 6 | Decentral | DKE | 78.1129 | 44.1379 | 74.52 | 45.8172 | 78.1129 | 44.1379 | 81.7057 | 42.4586 | HTEH | 100 | °C | 5 |  | Decentral | DKE | 78.1129 | 44.1379 | 74.52 | 45.8172 | 78.1129 | 44.1379 | 81.7057 | 42.4586 |  | HTEH | 215 | °C | 488.15 | °K | 5 | 313.15 | °K |  | Heat pump, ambient | 2015 | 3.5 |  |  | 313.15 | 353.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.57438
7 | ANDELSSELSKABET OKSBØL VARMEVÆRK | 29189 | Decentral | DKW | 3.255% | 71.3 | 34.6 | 69.5 | 32.6 | 35.5531 | 17.53% | AUGUSTENBORG FJERNVARME A.M.B.A. | 0.9223% | 72 | 36.8 | 72 | 33.3 | 36.2191 | 25.4% | 19.873 | 7 | Decentral | DKW | 72.6728 | 38.255 | 70.699 | 39.6651 | 72.6728 | 38.255 | 74.6466 | 36.845 | Carnot Eff. | 0.55 |  |  |  | Decentral | DKW | 72.6728 | 38.255 | 70.699 | 39.6651 | 72.6728 | 38.255 | 74.6466 | 36.845 |  | Lorentz Eff. |  |  | 0.57138 | [5 empty] | Heat pump, ambient | 2020 | 3.6 | 3.5 | 3.8 | 313.15 | 353.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.59079 | 0.57438 | 0.62361
8 | ANS FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | AULUM FJERNVARME A.M.B.A. | 0.1813% | 72 | 35 | 72 | 32 |  | 28.26% | 20.938 | 8 | [10 empty] | Off-Design Eff. | 1 | [14 empty] | Off-Design Eff. |  |  | 1 | [5 empty] | Heat pump, ambient | 2030 | 3.8 |  |  | 313.15 | 353.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.62361
9 | ANSAGER VARMEVÆRK | 29189 | Decentral | DKW | 2.685% | 76 | 38 | 76 | 34 | 41.4162 | 24.04% | BALLING FJERNVARMEVÆRK A.M.B.A. |  | 71 | 39 | 74 | 36 | 36.1715 | 28.35% | 7.945 | 9 | LTMEH |  | Spring | Summer | Autumn | Winter | [11 empty] | SPRING |  | SUMMER |  | AUTUMN |  | WINTER | [11 empty] | Heat pump, ambient | 2050 | 4.1 | 3.5 | 4.5 | 313.15 | 353.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.67284 | 0.57438 | 0.73849
10 | ARDEN VARMEVÆRK AMBA | 29189 | Decentral | DKW | [7 empty] | BEDSTED FJERNVARME |  | 67 | 39 | 68 | 39 |  | 13.22% | 7.9772 | 10 | Central | DKE | 4.4147 | 4.7947 | 4.4147 | 4.0972 | [9 empty] | °K |  | Supp_temp_spr | Ret_temp_sspr | Supp_temp_summ | Ret_temp_summ | Supp_temp_aut | Ret_temp_aut | Supp_temp_wint | Ret_temp_wint | [10 empty] | Heat pump, ambient | 2015 | 3.5 |  |  | 313.15 | 353.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.57438
11 | ASSENS FJERNVARME A M B A | 29189 | Decentral | DKW | 0.7025% | 75 | 43 | 75 | 38 | 36.2183 | 24.02% | BILLUND VARMEVÆRK A.M.B.A. |  | 72 | 42 | 85 | 45 | 32.0713 | 16.57% | 65.0691 | 11 |  | DKW | 5.2238 | 5.714 | 5.2238 | 4.8186 | [9 empty] | Central | DKE | 355 | 322.0531 | 350.9853 | 322.3375 | 355 | 322.0531 | 359.0147 | 321.7687 | [10 empty] | Heat pump, ambient | 2020 | 4 | 3.5 | 4.5 | 313.15 | 348.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.63206 | 0.55305 | 0.71106
12 | ASTRUP KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | BINDSLEV FJERNVARME A.M.B.A. | 7.101% | 68 | 38 | 72 | 33 | 35.7853 | 28.13% | 8.951 | 12 | Decentral | DKE | 4.766 | 5.1697 | 4.766 | 4.4272 | [9 empty] | Central | DKW | 347.2362 | 314.1738 | 343.7159 | 315.7496 | 347.2362 | 314.1738 | 350.7566 | 312.598 | [10 empty] | Heat pump, ambient | 2030 | 4.8 |  |  | 308.15 | 343.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.6963
13 | ASÅ VARMEVÆRK V/POUL NIELSEN | 29189 | Decentral | DKW | 0% | 67 | 38 | 67 | 34 | 32.9449 | 25.54% | BJERRINGBRO VARMEVÆRK A.M.B.A. |  | 69 | 41 | 72 | 36 | 34.4 | 18.22% | 63.791 | 13 |  | DKW | 5.409 | 5.6935 | 5.409 | 5.1542 | [9 empty] | Decentral | DKE | 351.2629 | 317.2879 | 347.67 | 318.9672 | 351.2629 | 317.2879 | 354.8557 | 315.6086 | [10 empty] | Heat pump, ambient | 2050 | 6 | 3.5 | 7 | 303.15 | 333.15 | 280.65 | 275.65 | 0-18 | ´5-10 | 0.75061 | 0.43786 | 0.87571
14 | AUGUSTENBORG FJERNVARME A M B A | 29189 | Decentral | DKW | 0.9223% | 72 | 36.8 | 72 | 33.3 | 36.2191 | 25.4% | BOGENSE FORSYNINGSSELSKAB A.M.B.A. |  | 68 | 38 | 66 | 35 |  | 20.64% | 28.1486 | 14 | [15 empty] | Decentral | DKW | 345.8228 | 311.405 | 343.849 | 312.8151 | 345.8228 | 311.405 | 347.7966 | 309.995 | [10 empty] | Waste heat 20 Degrees | 2015 | 4.4 |  |  | 313.15 | 353.15 | 293.15 | 288.15 |  |  | 0.55678
15 | AULUM FJERNVARME AMBA | 29189 | Decentral | DKW | 0.1813% | 72 | 35 | 72 | 32 |  | 28.26% | BORUP VARMEVÆRK |  | 75 | 45 | 80 | 42 |  | 23.43% | 23.058 | 15 | [35 empty] | Waste heat 20 Degrees | 2020 | 5 | 4.4 | 6 | 313.15 | 348.15 | 293.15 | 288.15 |  |  | 0.60087 | 0.52876 | 0.72104
16 | AUNING VARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | BOULSTRUP-HOU KRAFTVARMEVÆRK A.M.B.A. |  | 68 | 42 | 71 | 39 |  | 36.49% | 10.43 | 16 | MTEH |  | Spring | Summer | Autumn | Winter | [9 empty] | LTMEH |  | Spring | Summer | Autumn | Winter | [14 empty] | Waste heat 20 Degrees | 2030 | 6 |  |  | 308.15 | 343.15 | 293.15 | 288.15 |  |  | 0.63983
17 | Avedøre Fjernvarme | 55606 | Central | DKE | 0% | 165 | 100 | 165 | 70 |  | 23.9% | BRAMMING FJERNVARME A.M.B.A. |  | 68 | 0 | 68 | 0 |  |  |  | 17 | Central | DKE | 6.303 | 7.1327 | 6.303 | 5.659 | [9 empty] | Central | DKE | 4.6634 | 4.8493 | 4.6634 | 4.4937 | [14 empty] | Waste heat 20 Degrees | 2050 | 7.4 | 4.4 | 8.5 | 303.15 | 333.15 | 293.15 | 288.15 |  |  | 0.63479 | 0.37744 | 0.72915
18 | Ballen-Brundby Fjernvarme Amba | 23795 | Decentral | DKW | [7 empty] | BRANDE FJERNVARME AMBA |  | 70 | 0 | 75 | 0 |  |  |  | 18 |  | DKW | 8.1574 | 9.4595 | 8.1574 | 7.1873 | [10 empty] | DKW | 5.6165 | 5.7544 | 5.6165 | 5.4875 | [14 empty] | Waste heat 40 Degrees | 2015 | 7 |  |  | 313.15 | 353.15 | 313.15 | 298.15 |  |  | 0.57138
19 | BALLING FJERNVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 71 | 39 | 74 | 36 | 36.1715 | 28.35% | BREDEBRO VARMEVÆRK A.M.B.A. | 1.927% | 65 | 65 | 72 | 72 | 37.5467 |  | 0.009941 | 19 | Decentral | DKE | 7.0677 | 8.0228 | 7.0677 | 6.3292 | [9 empty] | Decentral | DKE | 5.1336 | 5.2435 | 5.1336 | 5.0302 | [14 empty] | Waste heat 40 Degrees | 2020 | 9 | 7 | 12 | 313.15 | 348.15 | 313.15 | 298.15 |  |  | 0.67437 | 0.52451 | 0.89916
20 | BEDSTED FJERNVARME AMBA V/KNUD OLE HENRIKSEN | 29189 | Decentral | DKW | 0% | 67 | 39 | 68 | 39 |  | 13.22% | BREDSTEN-BALLE KRAFTVARMEVÆRK |  | 72 | 42 | 74 | 40 | 32.5958 | 25.66% | 10.776 | 20 |  | DKW | 8.6316 | 9.4022 | 8.6316 | 7.9844 | [10 empty] | DKW | 5.9554 | 5.9943 | 5.9554 | 5.918 | [14 empty] | Waste heat 40 Degrees | 2030 | 12 |  |  | 308.15 | 343.15 | 313.15 | 298.15 |  |  | 0.72839
21 | Billund Varmeværk A.m.b.a. | 29189 | Decentral | DKW | 0% | 72 | 42 | 85 | 45 | 32.0713 | 16.57% | BROAGER FJERNVARMESELSKAB A.M.B.A. | 5.004% | 72 | 38 | 76 | 33 | 40.2477 | 26.53% | 17.737 | 21 | [35 empty] | Waste heat 40 Degrees | 2050 | 18 | 7 | 20 | 303.15 | 333.15 | 313.15 | 298.15 |  |  | 0.69786 | 0.27139 | 0.7754
22 | BINDSLEV FJERNVARME A M B A | 29189 | Decentral | DKW | 7.101% | 68 | 38 | 72 | 33 | 35.7853 | 28.13% | BROVST FJERNVARME A.M.B.A. |  | 75 | 39 | 80 | 36 |  | 30.85% | 21.452 | 22
23 | BJERRINGBRO VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 69 | 41 | 72 | 36 | 34.4 | 18.22% | BRÆDSTRUP FJERNVARME A.M.B.A. | 1.946% | 68 | 38 | 75 | 35 | 36.0003 |  |  | 23 | Future COP Values |  | Based on similar assumptions for DH temperatures as stated in the technology catalog 2017 from the Danish energy agency | [12 empty] | MTEH |  | Spring | Summer | Autumn | Winter
24 | BLENSTRUP KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | BRØNDBY FJERNVARME A.M.B.A. | 13.58% | 70.3 | 47.6 | 75.5 | 48.5 |  | 13.32% | 226.101 | 24 | [15 empty] | Central | DKE | 6.8651 | 7.2952 | 6.8651 | 6.4883 | [15 empty] | 59 | 151 | 243 | 334 | 365
25 | BLÅHØJ ENERGISELSKAB A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | BRØRUP FJERNVARME A.M.B.A. |  | 65 | 35 | 65 | 33 |  | 16.8% | 20.6322 | 25 |  | SPRING |  | SUMMER |  | AUTUMN |  | WINTER | [8 empty] | DKW | 9.2898 | 9.6911 | 9.2898 | 8.9273
26 | Bogense Forsyningsselskab | 29188 | Decentral | DKW | 0% | 68 | 38 | 66 | 35 |  | 20.64% | BÆKMARKSBRO VARMEVÆRK A.M.B.A. |  | 69 | 0 | 78 | 0 |  |  |  | 26 |  | Supp_temp_spr | Ret_temp_sspr | Supp_temp_summ | Ret_temp_summ | Supp_temp_aut | Ret_temp_aut | Supp_temp_wint | Ret_temp_wint | [6 empty] | Decentral | DKE | 7.9908 | 8.273 | 7.9908 | 7.7325 | [14 empty] | Historical average temperatures denmark
27 | BORNHOLMS VARME A/S | 26696 | Decentral | DKE | [7 empty] | BÆLUM VARMEVÆRK A.M.B.A. |  | 70 | 43 | 76 | 36 |  | 26.72% | 6.29 | 27 | 2020 | 75 | 40 | 71.7964 | 41.1489 | 75 | 40 | 78.2036 | 38.8511 | [7 empty] | DKW | 10.3031 | 10.4253 | 10.3031 | 10.1868 | [14 empty] | DKE | Winter | Spring | Summer | Autumn
28 | BORUP VARMEVÆRK A M B A | 29189 | Decentral | DKE | 0% | 75 | 45 | 80 | 42 |  | 23.43% | CHRISTIANSFELD FJERNVARMESELSKAB A.M.B.A | 3.024% | 70 | 39 | 70 | 36 | 34.8294 | 24.54% | 17.063 | 28 | 2030 | 70 | 35 | 67.1713 | 36.323 | 70 | 35 | 72.8287 | 33.677 | [26 empty] | Air | #REF! | 6.17 | #REF! | #REF!
29 | Boulstrup-Hou Kraftvarmeværk AMBA | 32264 | Central | DKW | 0% | 68 | 42 | 71 | 39 | 0 | 36.49% | DAGNÆS-BÆKKELUND VARMEVÆRK A.M.B.A. |  | 65 | 48 | 67 | 43 | 27.1276 | 32.37% | 36.836 | 29 | 2050 | 60 | 30 | 57.7849 | 31.1249 | 60 | 30 | 62.2151 | 28.8751 | [26 empty] | Soil | #REF! | 5.4 | #REF! | #REF!
30 | Boulstrup-Hou Kraftvarmeværk AMBA | 32264 | Decentral | DKW | 0% | 68 | 42 | 71 | 39 | 0 | 36.49% | DURUP FJERNVARME | 1.843% | 68 | 36 | 72 | 36 | 34.2865 | 16.59% | 7.506 | 30 | [15 empty] | Future COP Values |  | Based on similar assumptions for DH temperatures as stated in the technology catalog 2017 from the Danish energy agency | [16 empty] | https://www.seatemperature.org/europe/denmark/ | Water | 3.2333 | 6.5 | 16.6667 | 12.3333
31 | Brande Fjernvarme | 29189 | Decentral | DKW | 0% | 70 | 0 | 75 | 0 |  | 22.8% | DYBVAD VARMEVÆRK A.M.B.A. |  | 70 | 0 | 76 | 0 | 47.2105 | 22.41% | 6.751 | 31 | LTMEH | Spring | Summer | Autumn | Winter
32 | Bredsten-Balle Kraftvarmeværk amba | 29189 | Decentral | DKW | 0% | 72 | 42 | 74 | 40 | 32.5958 | 25.66% | EBELTOFT FJERNVARMEVÆRK A.M.B.A. |  | 75 | 41 | 75 | 36 | 40.5978 | 21.78% | 42.585 | 32 | 2020 | 5.1114 | 5.5313 | 5.1114 | 4.7567 | [11 empty] | SPRING |  | SUMMER |  | AUTUMN |  | WINTER | [12 empty] | DKW | Winter | Spring | Summer | Autumn
33 | BROAGER FJERNVARMESELSKAB AMBA | 29189 | Decentral | DKW | 5.004% | 72 | 38 | 76 | 33 | 40.2477 | 26.53% | EGEDAL FJERNVARME A/S |  | 65 | 70 | 70 | 70 |  |  |  | 33 | 2030 | 5.8025 | 6.2949 | 5.8025 | 5.3878 | [11 empty] | Supp_temp_spr | Ret_temp_sspr | Supp_temp_summ | Ret_temp_summ | Supp_temp_aut | Ret_temp_aut | Supp_temp_wint | Ret_temp_wint | [11 empty] | Air | #REF! | 6.0428 | #REF! | #REF!
34 | BROVST FJERNVARME ANDELSSELSKAB | 29189 | Decentral | DKW | 0% | 75 | 39 | 80 | 36 |  | 30.85% | EJBY FJERNVARME A.M.B.A. | 0.9067% | 68 | 36 | 68 | 36 | 33.3741 | 24.48% | 11.885 | 34 | 2050 | 8.0862 | 8.8893 | 8.0862 | 7.4242 | [10 empty] | 2020 | 75 | 40 | 74.2978 | 40.1565 | 75 | 40 | 75.7022 | 39.8435 | [11 empty] | Soil | #REF! | 5.3188 | #REF! | #REF!
35 | BRÆDSTRUP FJERNVARME A M B A | 29189 | Decentral | DKW | 1.946% | 68 | 38 | 75 | 35 | 36.0003 | 22.8% | EJSING FJERNVARMEFORSYNING A.M.B.A. |  | 69 | 41 | 70 | 39 | 21.2869 | 32.59% | 1.843 | 35 | [15 empty] | 2030 | 70 | 35 | 69.3909 | 35.1732 | 70 | 35 | 70.6091 | 34.8268 | [10 empty] | https://www.seatemperature.org/europe/denmark/ | Water | 3.8667 | 6.6667 | 16.4333 | 12.3333
36 | BRØNDBY FJERNVARME A M B A | 65113 | Central | DKE | 13.58% | 70.3 | 47.6 | 75.5 | 48.5 | 0 | 13.32% | EJSTRUPHOLM VARMEVÆRK | 3.356% | 70 | 32 | 70 | 32 | 36.5605 | 18.97% | 13.441 | 36 | [15 empty] | 2050 | 60 | 30 | 59.5209 | 30.1474 | 60 | 30 | 60.4791 | 29.8526
37 | BRØNDBY FJERNVARME A M B A | 65120 | Central | DKE | 13.58% | 70.3 | 47.6 | 75.5 | 48.5 | 0 | 13.32% | ELLIDSHØJ-FERSLEV KRAFTVARMEVÆRK |  | 78 | 0 | 83 | 0 |  | 41.86% | 6.248 | 37 | MTEH | Spring | Summer | Autumn | Winter | [11 empty] | SPRING |  | SUMMER |  | AUTUMN |  | WINTER
38 | BRØNDERSLEV VARME A/S | 29189 | Decentral | DKW | [7 empty] | ENERGI VIBORG KRAFTVARME A/S |  | 80 | 44 | 93 | 41 |  | 2.5% | 286.104 | 38 | 2020 | 7.8793 | 8.9566 | 7.8793 | 7.0468 | [11 empty] | Supp_temp_spr | Ret_temp_sspr | Supp_temp_summ | Ret_temp_summ | Supp_temp_aut | Ret_temp_aut | Supp_temp_wint | Ret_temp_wint
39 | BRØRUP FJERNVARME A M B A | 29189 | Decentral | DKW | 0% | 65 | 35 | 65 | 33 |  | 16.8% | ENERGIMIDT - ENERGIGRUPPEN JYLLAND A/S |  | 70 | 40 | 72 | 36 | 32.4087 | 19.84% | 448.438 | 39 | 2030 | 9.7116 | 11.2208 | 9.7116 | 8.5764 | [10 empty] | 2020 | 348.15 | 313.15 | 347.4478 | 313.3065 | 348.15 | 313.15 | 348.8522 | 312.9935
40 | Bækmarksbro Varmeværk A.M.B.A. | 29189 | Decentral | DKW | 0% | 69 | 0 | 78 | 0 |  | 22.8% | ESBJERG FORSYNING A/S |  | 75 | 40 | 85 | 38 |  | 10.11% | 842.695 | 40 | 2050 | 18.8732 | 24.0868 | 18.8732 | 15.5505 | [10 empty] | 2030 | 343.15 | 308.15 | 342.5409 | 308.3232 | 343.15 | 308.15 | 343.7591 | 307.9768
41 | BÆLUM VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 70 | 43 | 76 | 36 |  | 26.72% | FARSØ VARMEVÆRK A.M.B.A. |  | 72 | 40 | 78 | 35 | 54.93 | 28.08% | 32.596 | 41 | [15 empty] | 2050 | 333.15 | 303.15 | 332.6709 | 303.2974 | 333.15 | 303.15 | 333.6291 | 303.0026
42 | BØVLING VARMEVÆRK | 29189 | Decentral | DKW | [7 empty] | FAXE FJERNVARMESELSKAB A.M.B.A. |  | 72 | 0 | 80 | 0 |  |  |  | 42
43 | CHR FELD FJERNVS AMBA | 29189 | Decentral | DKW | 3.024% | 70 | 39 | 70 | 36 | 34.8294 | 24.54% | FENSMARK FJERNVARMEVÆRK A.M.B.A. | 0.4451% | 72 | 42 | 75 | 39 |  | 28.11% | 16.081 | 43 |  |  | LTMEH | [12 empty] | LTMEH | Spring | Summer | Autumn | Winter
44 | Christian Højer | 29188 | Decentral | DKE | [7 empty] | FILSKOV ENERGISELSKAB | 26.08% | 75 | 42 | 85 | 42 |  |  |  | 44 |  |  | W | 2020 | 4.7567 | [10 empty] | 2020 | 6.6445 | 6.6909 | 6.6445 | 6.599
45 | DAGNÆS-BÆKKELUND VARMEVÆRK | 29189 | Decentral | DKW | 0% | 65 | 48 | 67 | 43 | 27.1276 | 32.37% | FJERNVARME FYN A/S |  | 75 | 42 | 85 | 36 | 34.8028 | 17.17% | 1590.292 | 45 |  |  | R | 2020 | 5.1114 | [10 empty] | 2030 | 8.3083 | 8.363 | 8.3083 | 8.2545
46 | DONG ENERGY A/S | 29189 | Decentral | DKE | [7 empty] | FJERNVARMECENTRALEN AVEDØRE HOLME |  | 165 | 100 | 165 | 70 |  | 23.9% | 71.2153 | 46 |  |  | S | 2020 | 5.5313 | [10 empty] | 2050 | 10.5146 | 10.5878 | 10.5146 | 10.4425
47 | DONG ENERGY GASFORSYNING A/S | 29189 | Decentral | DKW | [7 empty] | FJERRITSLEV FJERNVARME |  | 76 | 0 | 80 | 0 |  | 30.66% | 43.52 | 47 |  |  | F | 2020 | 5.1114
48 | DONG GAS DISTRIBUTION A/S | 29189 | Decentral | DKW | [7 empty] | FREDERICIA FJERNVARME A.M.B.A. |  | 65 | 45 | 75 | 41 | 31.6177 | 12.36% | 238.4275 | 48 |  |  | W | 2030 | 5.3878
49 | DRONNINGLUND FJERNVARMEVÆRK AMBA | 29189 | Decentral | DKW | [7 empty] | FREDERIKS VARMEVÆRK A.M.B.A. | 2.405% | 70 | 40 | 73 | 33 | 35.0766 | 25.85% | 11.494 | 49 |  |  | R | 2030 | 5.8025 | [10 empty] | MTEH | Spring | Summer | Autumn | Winter
50 | DTU-HF A.m.b.a. | 11715 | Central | DKE | [7 empty] | FREDERIKSBERG FJERNVARME A/S |  | 75.9 | 49.2 | 82.5 | 47.9 |  | 7.243% | 663.69 | 50 |  |  | S | 2030 | 6.2949 | [10 empty] | 2020 | 11.0092 | 11.1427 | 11.0092 | 10.8792
51 | DURUP FJERNVARME | 29189 | Decentral | DKW | 1.843% | 68 | 36 | 72 | 36 | 34.2865 | 16.59% | FREDERIKSHAVN VARME A/S | 2.706% | 75 | 70 | 85 | 75 |  | 17.93% | 167.646 | 51 |  |  | F | 2030 | 5.8025 | [10 empty] | 2030 | 15.5593 | 15.7609 | 15.5593 | 15.3633
52 | Dybvad Varmeværk | 29189 | Decentral | DKW | 0% | 70 | 0 | 76 | 0 | 47.2105 | 22.41% | FUGLEBJERG FJERNVARME |  | 69 | 44 | 75 | 41 |  |  |  | 52 |  |  | W | 2050 | 7.4242 | [10 empty] | 2050 | 28.4139 | 28.9798 | 28.4139 | 27.8709
53 | E.ON DANMARK A/S | 29188 | Decentral | DKE | [7 empty] | FUR KRAFTVARMEVÆRK AMBA |  | 70 | 0 | 80 | 0 |  |  |  | 53 |  |  | R | 2050 | 8.0862
54 | E.ON DANMARK A/S | 29189 | Decentral | DKE | [7 empty] | GALTEN VARMEVÆRK |  | 75 | 37 | 78 | 37 |  | 17.36% | 32.722 | 54 |  |  | S | 2050 | 8.8893 | [14 empty] | DKE | DKE | DKW | DKW | [5 empty] | DKE | DKE | DKW | DKW
55 | E.ON VARME DANMARK ApS | 18957 | Decentral | DKE | [7 empty] | GANDRUP VESTER-HASSING VARMEFORSYNING |  | 72 | 36 | 74 | 37 |  | 30.98% | 30.313 | 55 |  |  | F | 2050 | 8.0862 | [11 empty] | LTMEH |  |  | Central | Decentral | Central | Decentral |  |  | LTMEH |  |  | Central | Decentral | Central | Decentral
56 | E.ON VARME DANMARK ApS | 29188 | Decentral | DKE | [7 empty] | GAUERSLUND FJERNVARME A.M.B.A. |  | 67.9 | 44 | 68.52 | 38 |  | 25.01% | 55.343 | 56 |  |  | MTEH | [14 empty] | W | 2015 | 4.4937 | 5.0302 | 5.4875 | 5.918 |  |  |  | W | 2015 | 4.4937 | 5.0302 | 5.4875 | 5.918
57 | E.ON VARME DANMARK ApS | 29189 | Decentral | DKE | [7 empty] | GELSTED FJERNVARME | 5% | 68 | 33 | 72 | 35 | 35.9643 | 27.61% | 6.877 | 57 |  |  | W | 2020 | 7.0468 | [12 empty] | R | 2015 | 4.6634 | 5.1336 | 5.6165 | 5.9554 |  |  |  | R | 2015 | 4.6634 | 5.1336 | 5.6165 | 5.9554
58 | EBELTOFT FJERNVARMEVÆRK | 29189 | Decentral | DKW | 0% | 75 | 41 | 75 | 36 | 40.5978 | 21.78% | GENNER-HELLEVAD-HOVSLUND | 1.219% | 65 | 40 | 72 | 38 | 28.4537 | 40.1% | 7.769 | 58 |  |  | R | 2020 | 7.8793 | [12 empty] | S | 2015 | 4.8493 | 5.2435 | 5.7544 | 5.9943 |  |  |  | S | 2015 | 4.8493 | 5.2435 | 5.7544 | 5.9943
59 | Egtved Varmeværk A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | GEV VARME A/S | 1.666% | 70 | 45 | 82 | 37 | 34.7099 | 23.96% | 80.909 | 59 |  |  | S | 2020 | 8.9566 | [12 empty] | F | 2015 | 4.6634 | 5.1336 | 5.6165 | 5.9554 |  |  |  | F | 2015 | 4.6634 | 5.1336 | 5.6165 | 5.9554
60 | Ejby Fjernvarmecentral AMBA | 29189 | Decentral | DKW | 0.9067% | 68 | 36 | 68 | 36 | 33.3741 | 24.48% | GILLELEJE FJERNVARME A.M.B.A. | 6.053% | 76 | 43 | 77 | 41 | 36.9514 | 32.88% | 27.059 | 60 |  |  | F | 2020 | 7.8793 | [12 empty] | W | 2020 | 6.599 | 6.599 | 6.599 | 6.599 |  |  |  | W | 2020 | 5.3037 | 5.937 | 6.4767 | 6.9848
61 | Ejsing Fjernvarmeforsyning A.M.B.A | 29189 | Decentral | DKW | 0% | 69 | 41 | 70 | 39 | 21.2869 | 32.59% | GJØL PRIVATE KRAFTVARMEVÆRK |  | 67 | 36 | 71 | 34 | 35.5861 | 33.61% | 5.707 | 61 |  |  | W | 2030 | 8.5764 | [12 empty] | R | 2020 | 6.6445 | 6.6445 | 6.6445 | 6.6445 |  |  |  | R | 2020 | 5.5039 | 6.0589 | 6.6288 | 7.0289
62 | Ejstrupholm Varmeværk A. m. b. a. | 29189 | Decentral | DKW | 3.356% | 70 | 32 | 70 | 32 | 36.5605 | 18.97% | GLOSTRUP FORSYNING |  | 80 | 50 | 90 | 55 | 26.4624 | 10.82% | 70.814 | 62 |  |  | R | 2030 | 9.7116 | [12 empty] | S | 2020 | 6.6909 | 6.6909 | 6.6909 | 6.6909 |  |  |  | S | 2020 | 5.7233 | 6.1887 | 6.7916 | 7.0748
63 | Ellehavegaard Energy I/S v/Peter og Inge-Merete Palle Pedersen | 29188 | Decentral | DKE | [7 empty] | GLYNGØRE FJERNVARMEVÆRK | 1.212% | 68 | 40 | 75 | 37 | 30.6885 | 20.06% | 3.974 | 63 |  |  | S | 2030 | 11.2208 | [12 empty] | F | 2020 | 6.6445 | 6.6445 | 6.6445 | 6.6445 |  |  |  | F | 2020 | 5.5039 | 6.0589 | 6.6288 | 7.0289
64 | ELLIDSHØJ-FERSLEV KRAFTVARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 78 | 0 | 83 | 0 |  | 41.86% | GRAM FJERNVARME |  | 75 | 36 | 75 | 34 |  | 27.61% | 18.247 | 64 |  |  | F | 2030 | 9.7116 | [12 empty] | W | 2030 | 6.599 | 6.599 | 6.599 | 6.599 |  |  |  | W | 2030 | 5.7286 | 6.4125 | 6.9955 | 7.5443
65 | ENERGIGRUPPEN JYLLAND VARME A/S | 29189 | Central | DKW | [7 empty] | GRENAA VARMEVÆRK A.M.B.A. |  | 68 | 41 | 70 | 36 | 30.6483 | 19.96% | 120.095 | 65 |  |  | W | 2050 | 15.5505 | [12 empty] | R | 2030 | 6.6445 | 6.6445 | 6.6445 | 6.6445 |  |  |  | R | 2030 | 5.9448 | 6.5443 | 7.1599 | 7.5919
66 | ENERGIGRUPPEN JYLLAND VARME A/S | 29189 | Decentral | DKW | [7 empty] | GREVE FJERNVARMEVÆRK |  | 80.5 | 52.2 | 85 | 51.2 |  | 9.854% | 90.8377 | 66 |  |  | R | 2050 | 18.8732 | [12 empty] | S | 2030 | 6.6909 | 6.6909 | 6.6909 | 6.6909 |  |  |  | S | 2030 | 6.1818 | 6.6845 | 7.3357 | 7.6415
67 | ESBJERG VARME A/S | 29189 | Central | DKW | 0% | 75 | 40 | 85 | 38 |  | 10.11% | GRÆSTED FJERNVARME |  | 77 | 42 | 77 | 38 | 36.022 | 33.41% | 14.288 | 67 |  |  | S | 2050 | 24.0868 | [12 empty] | F | 2030 | 6.6445 | 6.6445 | 6.6445 | 6.6445 |  |  |  | F | 2030 | 5.9448 | 6.5443 | 7.1599 | 7.5919
68 | ESBJERG VARME A/S | 29189 | Decentral | DKW | 0% | 75 | 40 | 85 | 38 |  | 10.11% | GRÅSTEN VARME A/S |  | 75 | 40 | 75 | 38 |  | 27.94% | 23.992 | 68 |  |  | F | 2050 | 18.8732 | [12 empty] | W | 2050 | 10.4425 | 10.4425 | 10.4425 | 10.4425 |  |  |  | W | 2050 | 5.4884 | 6.1437 | 6.7022 | 7.228
69 | Farsø Varmeværk A M B A | 29189 | Decentral | DKW | 0% | 72 | 40 | 78 | 35 | 54.93 | 28.08% | GULDBORGSUND FORSYNING VARME |  | 78 | 45 | 84 | 40 | 38.6488 | 25.35% | 164.407 | 69 | [17 empty] | R | 2050 | 10.5146 | 10.5146 | 10.5146 | 10.5146 |  |  |  | R | 2050 | 5.6956 | 6.27 | 6.8597 | 7.2737
70 | FARUM FJERNVARME A M B A | 29188 | Decentral | DKE | [7 empty] | GYLLING-ØRTING-FALLING KRAFTVARMEVÆRK | 2.975% | 65 | 40 | 75 | 39 |  | 39.01% | 7.776 | 70 | [17 empty] | S | 2050 | 10.5878 | 10.5878 | 10.5878 | 10.5878 |  |  |  | S | 2050 | 5.9227 | 6.4043 | 7.0282 | 7.3212
71 | FAXE FJERNVARMESELSKAB A M B A | 29188 | Decentral | DKE | 0% | 72 | 0 | 80 | 0 |  | 22.8% | GØRDING VARMEVÆRK A.M.B.A. |  | 75 | 35 | 80 | 35 | 36.9254 | 24.81% | 13.4075 | 71 | [17 empty] | F | 2050 | 10.5146 | 10.5146 | 10.5146 | 10.5146 |  |  |  | F | 2050 | 5.6956 | 6.27 | 6.8597 | 7.2737
72 | FELDBORG KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | HADERSLEV FJERNVARME |  | 75 | 42 | 82 | 40 |  | 15.91% | 122.861 | 72 | [28 empty] | DKE | DKE | DKW | DKW
73 | FENSMARK FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKE | 0.4451% | 72 | 42 | 75 | 39 |  | 28.11% | HADSTEN VARMEVÆRK | 0.1751% | 64 | 45 | 78 | 39 | 41.3415 | 23.94% | 51.596 | 73 | [25 empty] | 0 |  |  | Central | Decentral | Central | Decentral
74 | FERRITSLEV FJERNVARME A.M.B.A. | 29188 | Decentral | DKW | [7 empty] | HADSUND BY'S FJERNVARMEVÆRK A.M.B.A. |  | 68.4 | 38.1 | 73.3 | 33.1 | 45.6257 | 23.4% | 48.467 | 74 | [27 empty] | 2015 | 4.6674 | 5.1352 | 5.6187 | 5.9558
75 | FFV VARME A/S | 29188 | Decentral | DKW | [7 empty] | HALS FJERNVARME A.M.B.A. |  | 70 | 38 | 71 | 34 | 39.1651 | 24.73% | 19.942 | 75 | [27 empty] | 2020 | 5.5087 | 6.0609 | 6.6315 | 7.0293
76 | FILSKOV ENERGISELSKAB A M B A | 29189 | Decentral | DKW | 26.08% | 75 | 42 | 85 | 42 |  | 22.8% | HALVRIMMEN-ARENTSMINDE KRAFTVARMEVÆRK |  | 75 | 40 | 80 | 37 |  |  |  | 76 | [27 empty] | 2030 | 5.95 | 6.5464 | 7.1627 | 7.5924
77 | FJELLERAD KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | [7 empty] | HAMMEL FJERNVARME A.M.B.A. |  | 71 | 42 | 77 | 40 |  | 22.89% | 89.88 | 77 | [27 empty] | 2050 | 5.7006 | 6.272 | 6.8625 | 7.2741
78 | FJERNVARME FYN A/S | 29188 | Central | DKW | 0% | 75 | 42 | 85 | 36 | 34.8028 | 17.17% | HAMMERSHØJ FJERNVARMEVÆRK |  | 73 | 42 | 73 | 38 | 29.8014 | 26.66% | 6.735 | 78
79 | FJERNVARME FYN A/S | 35209 | Central | DKW | 0% | 75 | 42 | 85 | 36 | 34.8028 | 17.17% | HARBOØRE VARMEVÆRK A.M.B.A. | 7.126% | 68 | 43 | 72 | 40 | 30.647 | 28.76% | 12.163 | 79
80 | FJERNVARME FYN A/S | 35209 | Decentral | DKW | 0% | 75 | 42 | 85 | 36 | 34.8028 | 17.17% | HASHØJ KRAFTVARMEFORSYNING |  | 78 | 0 | 78 | 0 |  |  |  | 80
81 | Fjernvarmecentralen Avedøre Holme | 55606 | Central | DKE | 0% | 165 | 100 | 165 | 70 |  | 23.9% | HASLEV FJERNVARME I.M.B.A. |  | 72 | 49.3 | 72 | 43.7 | 26.7388 | 22.8% | 49.869 | 81
82 | FJERNVARMEFORSYNINGEN I Ø TOREBY, TOREBY, SUNDBY OG NAGELSTI AMBA | 29188 | Decentral | DKE | 1.676% | 70 | 0 | 80 | 0 |  | 30.54% | HAVNDAL FJERNVARME A.M.B.A. | 1.208% | 65 | 43 | 75 | 38 | 33.7477 | 32.87% | 5.435 | 82
83 | FJERRITSLEV FJERNVARME | 29189 | Decentral | DKW | 0% | 76 | 0 | 80 | 0 |  | 30.66% | HELSINGE FJERNVARME | 3.241% | 70 | 45 | 80 | 40 | 31.777 | 26.89% | 30.839 | 83
84 | FLAUENSKJOLD FJERNV V/B NIELSEN | 29189 | Decentral | DKW | [7 empty] | HINNERUP FJERNVARME A.M.B.A. |  | 68 | 47 | 75 | 37 |  | 25.41% | 59.078 | 84
85 | FORSYNING HELSINGØR - VARME A/S | 64502 | Decentral | DKE | [7 empty] | HIRTSHALS FJERNVARME A.M.B.A. | 1.035% | 74 | 39 | 70 | 37 | 45.3782 | 27.42% | 48.844 | 85
86 | FORSYNING HELSINGØR SERVICE A/S | 29188 | Decentral | DKE | [7 empty] | HJALLERUP FJERNVARME ANDELSSELSKAB |  | 75 | 42 | 80 | 37 |  | 27.38% | 24.816 | 86
87 | FREDERICIA FJERNVARME A.M.B.A. | 69116 | Central | DKW | 0% | 65 | 45 | 75 | 41 | 31.6177 | 12.36% | HJORDKÆR FJERNVARMEVÆRK |  | 75 | 42 | 80 | 42 |  | 19.34% | 16.609 | 87
88 | FREDERIKS VARMEVÆRK A M B A | 29189 | Decentral | DKW | 2.405% | 70 | 40 | 73 | 33 | 35.0766 | 25.85% | HJØRRING VARMEFORSYNING |  | 68 | 45 | 76 | 41 | 33.2481 | 19.38% | 231.98 | 88
89 | Frederiksberg Forsyning | 11259 | Central | DKE | 0% | 75.9 | 49.2 | 82.5 | 47.9 |  | 7.243% | HOBRO VARMEVÆRK A.M.B.A. |  | 72.9 | 40.2 | 80.1 | 49.7 | 40.7172 | 21.34% | 40.255 | 89
90 | FREDERIKSHAVN VARME A/S | 29189 | Decentral | DKW | 2.706% | 75 | 70 | 85 | 75 | 0 | 17.93% | HOFOR |  | 82 | 48 | 71 | 50 |  | 15.44% | 3842.29 | 90
91 | FRØSTRUP VARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | HOLME-LUNDSHØJ FJERNVARME |  | 67 | 47 | 71 | 42 | 32.3748 | 27.11% | 41.026 | 91
92 | FUGLEBJERG FJERNVARMEVÆRK | 29189 | Decentral | DKE | 0% | 69 | 44 | 75 | 41 |  | 22.8% | HOLSTED VARMEVÆRK A.M.B.A. |  | 71 | 41 | 73 | 38 |  |  |  | 92
93 | FUR KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 70 | 0 | 80 | 0 |  | 22.8% | HOLTE FJERNVARME A.M.B.A. |  | 78 | 55 | 85 | 50 |  | 19.65% | 68.893 | 93
94 | Fårvang Varmeværk | 29189 | Decentral | DKW | [7 empty] | HORNBÆK FJERNVARME |  | 75 | 0 | 90 | 0 |  |  |  | 94
95 | GALTEN VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 75 | 37 | 78 | 37 |  | 17.36% | HORNSLET FJERNVARME A.M.B.A. |  | 66 | 38 | 80 | 36 |  |  |  | 95
96 | GANDRUP - VESTER-HASSING VARMEVÆRK A M B A | 29189 | Central | DKW | 0% | 72 | 36 | 74 | 37 | 0 | 30.98% | HORSENS VARMEVÆRK A.M.B.A. |  | 67 | 48 | 69 | 42 | 24.9809 | 12.65% | 187.4515 | 96
97 | GARTNERES VARMEFORSYNING I BELLINGE - FANGEL ApS | 35209 | Central | DKW | [7 empty] | HOVEDGAARD FJERNVARMEVÆRK A.M.B.A | 3.489% | 69 | 39 | 70 | 35 | 30.5936 | 27.33% | 10.1125 | 97
98 | GARTNERES VARMEFORSYNING I BELLINGE - FANGEL ApS | 35209 | Decentral | DKW | [7 empty] | HURUP FJERNVARME A.M.B.A. |  | 70 | 42 | 70 | 38 |  | 23.61% | 34.528 | 98
99 | GARTNERES VARMEFORSYNING I LINDVED ApS | 35209 | Central | DKW | [7 empty] | HVALPSUND KRAFTVARME A.M.B.A. |  | 70 | 0 | 75 | 0 |  |  |  | 99
100 | GARTNERES VARMEFORSYNING I LINDVED ApS | 35209 | Decentral | DKW | [7 empty] | HVALSØ KRAFTVARMEVÆRK A.M.B.A. |  | 72 | 45 | 80 | 42 |  | 28.73% | 21.323 | 100
101 | GARTNERES VARMEFORSYNING I ÅSUM OG LANGESKOV ApS | 35209 | Central | DKW | [7 empty] | HVIDBJERG FJERNVARME A.M.B.A. |  | 74.3 | 37.5 | 75.5 | 34.5 |  | 26.55% | 10.568 | 101
102 | GARTNERES VARMEFORSYNING I ÅSUM OG LANGESKOV ApS | 35209 | Decentral | DKW | [7 empty] | HVIDE SANDE FJERNVARME A.M.B.A. | 4.199% | 70 | 40 | 80 | 39 | 31.8891 | 31.77% | 26.252 | 102
103 | GARTNERNES FJERNVARMEFORSYNING I ODENSE NORD ApS | 35209 | Central | DKW | [7 empty] | HVIDEBÆK FJERNVARMEFORSYNING |  | 74 | 48 | 88 | 42 | 31.0184 | 37.25% | 14.243 | 103
104 | Gassum-Hvidsten Kraftvarmeværk AMBA | 29189 | Decentral | DKW | [7 empty] | HVIDOVRE MIDT A.M.B.A |  | 80 | 45 | 85 | 45 |  | 10.8% | 137.701 | 104
105 | GAUERSLUND FJERNVARME A M B A | 29189 | Central | DKW | 0% | 67.9 | 44 | 68.52 | 38 | 0 | 25.01% | HØJE TAASTRUP FJERNVARME A.M.B.A. |  | 74 | 52 | 82 | 48 |  | 17.57% | 262.696 | 105
106 | Gedser Fjernvarme | 29188 | Decentral | DKE | [7 empty] | HØNG VARMEVÆRK A.M.B.A. | 1.602% | 75 | 41 | 76 | 36 | 38.4303 | 28.14% | 29.482 | 106
107 | GEDSTED VARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | I/S SKIVE FJERNVARME | 3.807% | 68.7 | 49.7 | 70.8 | 46 | 22.1525 | 20.72% | 111.478 | 107
108 | GELSTED FJERNVARMECENTRAL | 29189 | Decentral | DKW | 5% | 68 | 33 | 72 | 35 | 35.9643 | 27.61% | IKAST VÆRKERNE VARME A/S |  | 69 | 40 | 73 | 36 | 42.0927 | 23.63% | 143.596 | 108
109 | GENNER, HELLEVAD OG HOVSLUND FORENEDE KRAFT- VARMEVÆRKER A.M.B.A | 29189 | Decentral | DKW | 1.219% | 65 | 40 | 72 | 38 | 28.4537 | 40.1% | ISHØJ VARMEVÆRK |  | 85 | 50 | 105 | 50 |  |  |  | 109
110 | Gentofte Kommune | 19438 | Central | DKE | [7 empty] | JELLING VARMEVÆRK |  | 70 | 36 | 73 | 34 | 37.8724 | 19.34% | 25.264 | 110
111 | Gentofte Kommune | 19438 | Decentral | DKE | [7 empty] | JERSLEV VARMEVÆRK A.M.B.A. |  | 72 | 0 | 72 | 0 |  |  |  | 111
112 | GERN VARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | JÆGERSPRIS KRAFTVARME A.M.B.A. | 1.125% | 67 | 40 | 80 | 38 | 32.0194 | 30.1% | 23.955 | 112
113 | GILLELEJE FJERNVARME A M B A | 29188 | Decentral | DKE | 6.053% | 76 | 43 | 77 | 41 | 36.9514 | 32.88% | KALUNDBORG FORSYNING A/S |  | 83.5 | 55.9 | 87.3 | 51.9 |  | 24.9% | 159.051 | 113
114 | GIVE FJERNVARME A M B A | 29189 | Decentral | DKW | [7 empty] | KARUP VARMEVÆRK A.M.B.A. |  | 68 | 0 | 70 | 0 |  |  |  | 114
115 | GJERLEV FJERNVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | KIBÆK VARMEVÆRK ANDELSSELSKAB |  | 65 | 33 | 65 | 34 |  | 26.87% | 23.041 | 115
116 | GJØL PRIVATE KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 67 | 36 | 71 | 34 | 35.5861 | 33.61% | KJELLERUP FJERNVARME |  | 68 | 31 | 70 | 32 | 36.0019 | 18.42% | 41.408 | 116
117 | Gladsaxe Kommunes Fjernvarmeforsyning | 62761 | Central | DKE | [7 empty] | KONGERSLEV FJERNVARMEVÆRK A.M.B.A. |  | 70 | 40 | 75 | 35 |  |  |  | 117
118 | GLAMSBJERG FJERNVARMECENTRAL | 29189 | Decentral | DKW | [7 empty] | KVÆRNDRUP FJERNVARME A.M.B.A. |  | 65 | 35 | 80 | 32 |  | 31.73% | 11.085 | 118
119 | GLOSTRUP VARME A/S | 65120 | Central | DKE | 0% | 80 | 50 | 90 | 55 | 26.4624 | 10.82% | LANGÅ VARMEVÆRK A.M.B.A. | 27.49% | 73 | 36 | 75 | 38 | 35.0471 | 27.31% | 14.858 | 119
120 | Gram Fjernvarme | 29189 | Decentral | DKW | 0% | 75 | 36 | 75 | 34 |  | 27.61% | LAURBJERG KRAFTVARMEVÆRK |  | 72 | 42 | 74 | 37 | 32.7679 | 32.58% | 5.3337 | 120
121 | GRENÅ VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 68 | 41 | 70 | 36 | 30.6483 | 19.96% | LEM VARMEVÆRK | 2.112% | 80 | 40 | 80 | 40 | 51.6168 | 11.33% | 39.615 | 121
122 | Greve Fjernvarmeværk A.m.b.a. | 44023 | Central | DKE | 0% | 80.5 | 52.2 | 85 | 51.2 |  | 9.854% | LEMVIG VARMEVÆRK A.M.B.A. |  | 66 | 37.5 | 75 | 36 | 28.2339 | 18.27% | 63.952 | 122
123 | GREVE STRANDBY FJERNVARMEVÆRK A.M.B.A | 44023 | Central | DKE | 0% | 80.5 | 52.2 | 85 | 51.2 |  | 9.854% | LYSTRUP FJERNVARME A.M.B.A. |  | 65 | 43 | 68 | 36 | 28.5629 | 25.22% | 64.025 | 123
124 | Grindsted El- og Varmeværk | 29189 | Decentral | DKW | [7 empty] | LØGSTRUP VARMEVÆRK A.M.B.A. | 2.451% | 70 | 36 | 75 | 33 | 35.4195 | 27.39% | 10.289 | 124
125 | Græsted Fjernvarme Amba Postboks 133 | 29188 | Decentral | DKE | 0% | 77 | 42 | 77 | 38 | 36.022 | 33.41% | LØGSTØR FJERNVARMEVÆRK A.M.B.A. |  | 75 | 43 | 80 | 40 |  | 26.87% | 61.57 | 125
126 | GRÅSTEN FJERNVARME A.M.B.A. | 29189 | Decentral | DKW | 0% | 75 | 40 | 75 | 38 |  | 27.94% | LØGUMKLOSTER FJERNVARME A.M.B.A. | 13.18% | 69 | 38 | 72 | 34 | 34.9594 | 24.6% | 22.402 | 126
127 | GULDBORGSUND VARME A/S | 29188 | Decentral | DKE | 0% | 78 | 45 | 84 | 40 | 38.6488 | 25.35% | LØKKEN VARMEVÆRK A.M.B.A |  | 70 | 42 | 72 | 35 | 31.903 | 24.15% | 20.863 | 127
128 | Gylling-Ørting-Falling Kraftvarmeværk A.M.B.A | 32264 | Decentral | DKW | 2.975% | 65 | 40 | 75 | 39 | 0 | 39.01% | LØNSTRUP VARMEFORSYNING A.M.B.A. |  | 68 | 44 | 70 | 39 | 27.0766 | 49.92% | 5.958 | 128
129 | Gårslev Fjernvarme A.M.B.A. | 29189 | Central | DKW | [7 empty] | LØSNING FJERNVARME A.M.B.A. |  | 66 | 37 | 65 | 35 |  | 22.1% | 18.379 | 129
130 | HADERSLEV FJERNVARME AMBA | 29189 | Decentral | DKW | 0% | 75 | 42 | 82 | 40 |  | 15.91% | MALLING VARMEVÆRK A.M.B.A. |  | 60.38 | 38 | 68 | 35 |  |  |  | 130
131 | HADERUP KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | MARSTAL FJERNVARME A.M.B.A. | 20.41% | 70 | 42 | 72 | 35 | 27.8131 | 24.18% | 21.1174 | 131
132 | HADSTEN VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0.1751% | 64 | 45 | 78 | 39 | 41.3415 | 23.94% | MIDDELFART FJERNVARME A.M.B.A. |  | 64 | 45 | 65 | 40 |  | 19.59% | 91.2261 | 132
133 | HADSUND FJERNVARMEVÆRK | 29189 | Decentral | DKW | 0% | 68.4 | 38.1 | 73.3 | 33.1 | 45.6257 | 23.4% | MIDTLANGELAND FJERNVARME A.M.B.A. |  | 73 | 0 | 73 | 0 |  |  |  | 133
134 | Hallund Kraftvarmeværk Amba | 29189 | Decentral | DKW | [7 empty] | MOSEDE FJERNVARMEVÆRK A.M.B.A |  | 73 | 0 | 73 | 0 | 28.5502 | 26.23% | 5.396 | 134
135 | HALS FJERNVARME A M B A | 29189 | Decentral | DKW | 0% | 70 | 38 | 71 | 34 | 39.1651 | 24.73% | MØLDRUP VARMEVÆRK | 7.394% | 70 | 34.5 | 72 | 33 | 33.6022 | 21.69% | 9.249 | 135
136 | HALSNÆS KOMMUNALE VARMEFORSYNING A/S | 29188 | Decentral | DKE | [7 empty] | MØLHOLM VARMEVÆRK |  | 63 | 63 | 73 | 73 | 20.7833 | 21.57% | 45.488 | 136
137 | Halvrimmen - Arentsminde Kraftvarmeværk A M B A | 29189 | Decentral | DKW | 0% | 75 | 40 | 80 | 37 |  | 22.8% | MØRKE FJERNVARME A.M.B.A. |  | 72 | 40 | 72 | 40 |  | 28.04% | 8.867 | 137
138 | HAMMEL FJERNVARME A M B A | 29189 | Decentral | DKW | 0% | 71 | 42 | 77 | 40 |  | 22.89% | MØRKØV VARMEVÆRK A.M.B.A. | 0.9431% | 67 | 42 | 81 | 34 | 32.4152 | 33.05% | 7.011 | 138
139 | HAMMERSHØJ FJERNVARMEVÆRK | 29189 | Decentral | DKW | 0% | 73 | 42 | 73 | 38 | 29.8014 | 26.66% | NIBE VARMEVÆRK A.M.B.A. |  | 71 | 0 | 79 | 0 |  |  |  | 139
140 | HANSTHOLM VARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | NIMTOFTE OG OMEGNS |  | 70 | 41 | 70 | 41 |  | 31.76% | 5.7953 | 140
141 | HARBOØRE VARMEVÆRK A.M.B.A. V/J.J. BIRCH | 29189 | Decentral | DKW | 7.126% | 68 | 43 | 72 | 40 | 30.647 | 28.76% | NORDBY FJERNVARME A.M.B.A. |  | 60 | 0 | 80 | 0 |  |  |  | 141
142 | Hashøj Kraftvarmeforsyning AMBA | 29188 | Decentral | DKE | 0% | 78 | 0 | 78 | 0 |  | 22.8% | NR. SNEDE VARMEVÆRK A.M.B.A. | 0.724% | 72 | 38 | 76 | 35 | 34.727 | 15.66% | 15.417 | 142
143 | HASLEV FJERNVARME I M B A | 29188 | Decentral | DKE | 0% | 72 | 49.3 | 72 | 43.7 | 26.7388 | 22.8% | NYBORG FORSYNING OG SERVICE A/S |  | 71 | 46 | 76 | 40 | 33.1533 | 20.93% | 149.246 | 143
144 | HAVNDAL FJERNVARME A M B A | 29189 | Decentral | DKW | 1.208% | 65 | 43 | 75 | 38 | 33.7477 | 32.87% | NYKØBING M. FJERNVARMEVÆRK A.M.B.A. |  | 74 | 40 | 74 | 38 | 36.8441 | 21.89% | 34.278 | 144
145 | HEDENSTED FJERNVARME | 29189 | Decentral | DKW | [7 empty] | NYKØBING S. VARMEVÆRK A.M.B.A. |  | 73 | 41 | 75 | 40 | 3.552 | 27.66% | 32.901 | 145
146 | HEJNSVIG VARMEVÆRK A M B A | 29189 | Decentral | DKW | [7 empty] | NYSTED VARMEVÆRK A.M.B.A |  | 67 | 67 | 71 | 71 | 33.0303 | 26.49% | 11.498 | 146
147 | HELSINGE FJERNVARME | 29188 | Decentral | DKE | 3.241% | 70 | 45 | 80 | 40 | 31.777 | 26.89% | NÆSTVED VARMEVÆRK A.M.B.A. |  | 75 | 53 | 85 | 47 | 34.1182 | 19.08% | 173.892 | 147
148 | HEMMET VARMEVÆRK AMBA | 29189 | Decentral | DKW | [7 empty] | NØRRE AABY KRAFTVARMEVÆRK A.M.B.A. |  | 68 | 40 | 70 | 37 |  | 23.82% | 18.7893 | 148
149 | HILLERØD VARME A/S | 29189 | Decentral | DKE | [7 empty] | NØRRE-ALSLEV FJERNVARMEVÆRK A.M.B.A. |  | 75 | 52 | 80 | 45 |  | 25.36% | 16.185 | 149
150 | HINNERUP FJERNVARME AMBA | 29189 | Decentral | DKW | 0% | 68 | 47 | 75 | 37 |  | 25.41% | ODDER VARMEVÆRK A.M.B.A. |  | 69.13 | 44.59 | 73.07 | 39.2 |  | 24.21% | 78.534 | 150
151 | HIRTSHALS FJERNVARME | 29189 | Decentral | DKW | 1.035% | 74 | 39 | 70 | 37 | 45.3782 | 27.42% | OKSBØL VARMEVÆRK | 3.255% | 71.3 | 34.6 | 69.5 | 32.6 | 35.5531 | 17.53% | 22.207 | 151
152 | HJALLERUP FJERNVARMEVÆRK | 29189 | Decentral | DKW | 0% | 75 | 42 | 80 | 37 |  | 27.38% | OUTRUP VARMEVÆRK A.M.B.A. |  | 70 | 40 | 74 | 36 | 30.2175 | 24.84% | 7.226 | 152
153 | HJORDKÆR FJERNVARMEVÆRK AMBA | 29189 | Central | DKW | 0% | 75 | 42 | 80 | 42 |  | 19.34% | OVERLUND FJERNVARMEVÆRK A.M.B.A. |  | 65 | 40 | 70 | 35 | 32.2096 | 24.17% | 9.969 | 153
154 | HJØRRING VARMEFORSYNING A M B A | 29189 | Decentral | DKW | 0% | 68 | 45 | 76 | 41 | 33.2481 | 19.38% | PADBORG FJERNVARME A.M.B.A. |  | 70 | 40 | 77 | 36 |  | 24.6% | 31.109 | 154
155 | HMN Naturgas I/S | 19501 | Central | DKE | [7 empty] | PINDSTRUP VARMEVÆRK |  | 75 | 38 | 84 | 40 |  | 30.19% | 5.849 | 155
156 | HMN Naturgas I/S | 29189 | Decentral | DKE | [7 empty] | PRÆSTØ FJERNVARME A.M.B.A. |  | 75 | 0 | 80 | 0 |  | 23.11% | 15.318 | 156
157 | HMN Naturgas I/S | 29189 | Decentral | DKW | [7 empty] | RAMSING-LEM-LIHME KRAFTVARMEVÆRK |  | 74 | 42 | 77 | 40 | 29.494 | 47.07% | 8.296 | 157
158 | HOBRO VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 72.9 | 40.2 | 80.1 | 49.7 | 40.7172 | 21.34% | RASK MØLLE VARMEVÆRK |  | 69 | 69 | 75 | 75 |  |  |  | 158
159 | Holeby Fjernvarme | 29188 | Decentral | DKE | [7 empty] | RIBE FJERNVARME A.M.B.A. | 6.305% | 68 | 39 | 70 | 37 | 34.6199 | 18.06% | 55.843 | 159
160 | HOLME-LUNDSHØJ FJERNVARMEV A M B A | 55133 | Central | DKW | 0% | 67 | 47 | 71 | 42 | 32.3748 | 27.11% | RINGE FJERNVARMESELSKAB |  | 69 | 42 | 79 | 40 | 31.9222 | 25.57% | 44.8728 | 160
161 | HOLSTED VARMEVÆRK | 29189 | Decentral | DKW | 0% | 71 | 41 | 73 | 38 |  | 22.8% | RINGKØBING FJERNVARMEVÆRK A.M.B.A. | 0.6503% | 67 | 39 | 67 | 35 |  | 25.36% | 76.629 | 161
162 | Hornbæk Fjernvarme Amba | 64502 | Decentral | DKE | 0% | 75 | 0 | 90 | 0 |  | 22.8% | RINGSTED KOMMUNALE VARMEFORSYNING |  | 75 | 45 | 85 | 48 |  | 18.81% | 105.136 | 162
163 | HORNSLET FJERNVARMESELSKAB AMBA | 29189 | Central | DKW | 0% | 66 | 38 | 80 | 36 |  | 17.37% | RISE FJERNVARME A.M.B.A. |  | 84 | 40 | 82 | 36 |  | 34.89% | 2.176 | 163
164 | HORSENS VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 67 | 48 | 69 | 42 | 24.9809 | 12.65% | ROSKILDE VARME A/S |  | 76 | 48 | 77 | 46 | 30.8916 | 19.9% | 342.709 | 164
165 | HOVEDGÅRD FJERNVARMEVÆRK AMBA | 29189 | Decentral | DKW | 3.489% | 69 | 39 | 70 | 35 | 30.5936 | 27.33% | RUNDHØJ FJERNVARME A.M.B.A. |  | 69 | 44 | 69 | 40 | 27.0593 | 17.44% | 8.806 | 165
166 | HUNDESTED VARMEVÆRK AMBA | 29188 | Decentral | DKE | [7 empty] | RVV A.M.B.A. |  | 73 | 47 | 75 | 44 | 29.4659 | 21.28% | 119.994 | 166
167 | Hundslund-Oldrup Kraftvarmeværk Amba | 32264 | Decentral | DKW | [7 empty] | RY VARMEVÆRK A.M.B.A. |  | 66 | 0 | 72 | 0 |  | 22.41% | 42.441 | 167
168 | HUNSEBY MAGLEMER VARMEVÆRK ApS | 29188 | Decentral | DKE | [7 empty] | RYE KRAFTVARMEVÆRK |  | 70 | 38 | 75 | 38 |  | 31.83% | 5.9517 | 168
169 | HURUP FJERNVARME | 29189 | Decentral | DKW | 0% | 70 | 42 | 70 | 38 |  | 23.61% | RYOMGAARD FJERNVARMEVÆRK A.M.B.A. |  | 70 | 40 | 70 | 40 |  | 27.65% | 12.987 | 169
170 | HVALSØ VARMEVÆRK | 29188 | Decentral | DKE | 0% | 72 | 45 | 80 | 42 | 0 | 28.73% | RÆHR FJERNVARME |  | 68 | 43 | 72 | 39 |  | 41.13% | 3.714 | 170
171 | Hvam-Gl Hvam Kraftvarmeværk AMBA | 29189 | Decentral | DKW | [7 empty] | RØDBY VARMEVÆRK A.M.B.A. | 4.146% | 75 | 52 | 80 | 45 | 33.0377 | 28.15% | 18.373 | 171
172 | HVIDBJERG FJERNVARME A M B A | 29189 | Decentral | DKW | 0% | 74.3 | 37.5 | 75.5 | 34.5 |  | 26.55% | RØDBYHAVN FJERNVARME A.M.B.A. |  | 78 | 49 | 86 | 46 | 28.5627 | 23.78% | 25.975 | 172
173 | Hvide Sande Fjernvarme A.M.B.A. | 29189 | Decentral | DKW | 4.199% | 70 | 40 | 80 | 39 | 31.8891 | 31.77% | RØDDING VARMECENTRAL |  | 77 | 39 | 77 | 39 | 37.8629 | 4.774% | 30.7 | 173
174 | HVIDEBÆK FJERNVARMEFORSYNING AMBA | 29189 | Central | DKE | 0% | 74 | 48 | 88 | 42 | 31.0184 | 37.25% | RØDKÆRSBRO FJERNVARMEVÆRK A.M.B.A. |  | 65 | 41 | 75 | 32 |  | 25.47% | 10.115 | 174
175 | HVIDEBÆK FJERNVARMEFORSYNING AMBA | 29189 | Decentral | DKE | 0% | 74 | 48 | 88 | 42 | 31.0184 | 37.25% | RØDOVRE KOMMUNALE FJERNVARMEFORSYNING |  | 70.2 | 47.3 | 75.9 | 46.7 | 26.8037 | 7.08% | 129.648 | 175
176 | HVIDOVRE FJERNVARMESELSKAB AMBA | 55606 | Central | DKE | 0% | 80 | 45 | 85 | 45 |  | 10.8% | SAKSKØBING FJERNVARMESELSKAB |  | 73 | 46 | 78 | 46 |  | 27.86% | 37.156 | 176
177 | HVIDOVRE FJERNVARMESELSKAB AMBA | 55606 | Decentral | DKE | 0% | 80 | 45 | 85 | 45 |  | 10.8% | SALTUM FJERNVARMEVÆRK A.M.B.A. |  | 72 | 35 | 75 | 35 | 33.5117 | 22.92% | 6.425 | 177
178 | HYLLINGE-MENSTRUP KRAFTVARMEVÆRKER A M B A | 29189 | Decentral | DKE | [7 empty] | SDR. OMME VARMEVÆRK AMBA | 3.628% | 65 | 40 | 68 | 34 | 32.3104 | 25.45% | 13.188 | 178
179 | HØJE TAASTRUP FJERNVARME A.M.B.A. | 19501 | Central | DKE | 0% | 74 | 52 | 82 | 48 |  | 17.57% | SDR.FELDING VARMEVÆRK |  | 65 | 0 | 70 | 0 |  |  |  | 179
180 | HØJE TAASTRUP FJERNVARME A.M.B.A. | 19501 | Decentral | DKE | 0% | 74 | 52 | 82 | 48 |  | 17.57% | SIG VARMEVÆRK |  | 68 | 36 | 70 | 33 |  | 26.02% | 4.883 | 180
181 | HØJSLEV NR SØBY FJERNVARME | 29189 | Decentral | DKW | [7 empty] | SILKEBORG FJERNVARME A/S |  | 66.1 | 44 | 69 | 39.5 | 27.7899 | 17.67% | 293.337 | 181
182 | HØNG VARMEVÆRK | 29189 | Decentral | DKE | 1.602% | 75 | 41 | 76 | 36 | 38.4303 | 28.14% | SINDAL VARMEFORSYNING A.M.B.A. | 0.3333% | 68 | 34 | 68 | 32 | 37.0409 | 25.27% | 21.676 | 182
183 | HØRBY VARMEVÆRK | 29189 | Decentral | DKW | [7 empty] | SKAGEN VARMEVÆRK A.M.B.A. | 1.269% | 67 | 46 | 83 | 41 | 29.1114 | 30.55% | 30.1 | 183
184 | Haarby Kraft-Varme Amba | 29189 | Decentral | DKW | [7 empty] | SKALS KRAFTVARMEVÆRK |  | 70 | 38 | 74 | 34 | 37.8922 | 28.47% | 12.944 | 184
185 | I/S Nordforbrænding | 29188 | Decentral | DKE | [7 empty] | SKANDERBORG - HØRNING FJERNVARME A.M.B.A |  | 65 | 39 | 75 | 37 |  | 22.54% | 193.186 | 185
186 | I/S Nordforbrænding | 70960 | Decentral | DKE | [7 empty] | SKJERN FJERNVARME CENTRAL |  | 72 | 37 | 68 | 33 | 34.041 | 22.78% | 54.465 | 186
187 | I/S SKIVE FJERNVARME | 29189 | Decentral | DKW | 3.807% | 68.7 | 49.7 | 70.8 | 46 | 22.1525 | 20.72% | SKOVLUND VARMEVÆRK A.M.B.A. |  | 63 | 38 | 70 | 36 |  |  |  | 187
188 | I/S Vestforbrændingen | 29188 | Decentral | DKE | [7 empty] | SKÆRBÆK FJERNVARME | 1.143% | 69 | 33 | 69 | 34 | 35.4515 | 20.37% | 21.701 | 188
189 | I/S Vestforbrændingen | 58271 | Decentral | DKE | [7 empty] | SKØRPING VARMEVÆRK A.M.B.A. |  | 80 | 37 | 89 | 36 |  | 25.27% | 27.65 | 189
190 | I/S Vestforbrændingen | 63640 | Decentral | DKE | [7 empty] | SLAGSLUNDE FJERNVARME A.M.B.A |  | 66 | 46 | 73 | 42 | 21.9905 | 40.52% | 3.2 | 190
191 | IKAST VÆRKERNE VARME A/S | 29189 | Central | DKW | 0% | 69 | 40 | 73 | 36 | 42.0927 | 23.63% | SMØRUM KRAFTVARME A.M.B.A. | 1.93% | 70 | 47 | 82 | 44 | 35.799 | 28.03% | 31.789 | 191
192 | IKAST VÆRKERNE VARME A/S | 29189 | Decentral | DKW | 0% | 69 | 40 | 73 | 36 | 42.0927 | 23.63% | SOLRØD FJERNVARMEVÆRK A.M.B.A |  | 68 | 45 | 73 | 41 | 31.8647 | 22.92% | 48.224 | 192
193 | INGSTRUP FJERNVARME ANDELSSELSKAB | 29189 | Decentral | DKW | [7 empty] | SPJALD FJERNVARME-OG VANDVÆRK A.M.B.A. | 0.7828% | 65 | 39 | 65 | 32 | 30.5092 | 28.25% | 10.003 | 193
194 | Ishøj Kommune | 11931 | Central | DKE | 0% | 85 | 50 | 105 | 50 |  | 17.37% | STRANDBY VARMEVÆRK A.M.B.A. |  | 70 | 35 | 70 | 31 | 36.8101 | 24.73% | 15.657 | 194
195 | JELLING VARMEVÆRK | 29189 | Decentral | DKW | 0% | 70 | 36 | 73 | 34 | 37.8724 | 19.34% | STRUER FORSYNING FJERNVARME A/S |  | 68.5 | 41 | 72 | 35 | 38.3741 | 23.75% | 102.064 | 195
196 | JERSLEV VARMEVÆRK | 29189 | Decentral | DKW | 0% | 72 | 0 | 72 | 0 |  | 22.8% | STØVRING KRAFTVARMEVÆRK A.M.B.A. | 1.15% | 69 | 0 | 72 | 0 |  | 23.71% | 43.473 | 196
197 | JETSMARK ENERGIVÆRK AMBA | 29189 | Decentral | DKW | [7 empty] | SVEBØLLE-VISKINGE FJERNVARMESELSKAB |  | 72 | 41 | 88 | 39 |  |  | 9.547 | 197
198 | JYDERUP VARME A/S | 29189 | Decentral | DKE | [7 empty] | SVENDBORG FJERNVARME A.M.B.A. |  | 85 | 45 | 85 | 45 |  | 22.41% | 131.66 | 198
199 | Jægerspris Kraftvarme A.m.b.a. | 29189 | Decentral | DKE | 1.125% | 67 | 40 | 80 | 38 | 32.0194 | 30.1% | SYDFALSTER VARMEVÆRK A.M.B.A. | 2.678% | 71.2 | 44.4 | 76.7 | 37.6 | 46.5164 | 33.45% | 19.467 | 199
200 | K/S DIFKO LXV | 26696 | Decentral | DKE | [7 empty] | SYDLANGELAND FJERNVARME A.M.B.A. |  | 80 | 40 | 80 | 38 |  | 42.86% | 17.269 | 200
201 | KALUNDBORG VARMEFORSYNING A/S | 29189 | Central | DKE | 0% | 83.5 | 55.9 | 87.3 | 51.9 |  | 24.9% | SÆBY VARMEVÆRK A.M.B.A. |  | 66 | 43 | 75 | 34 | 33.1896 | 27.48% | 56.097 | 201
202 | KARUP VARMEVÆRK | 29189 | Decentral | DKW | 0% | 68 | 0 | 70 | 0 |  | 22.8% | SØNDERBORG FJERNVARME A.M.B.A. |  | 79.43 | 46.72 | 80.96 | 41.73 |  | 24.48% | 223.6129 | 202
203 | KE VARME P/S | 64942 | Central | DKE | [7 empty] | SØNDERHOLM KRAFTVARMEVÆRK A.M.B.A. | 0.2082% | 71 | 39 | 75 | 39 |  | 31.18% | 4.85 | 203
204 | KERTEMINDE FORSYNING - VARME A/S | 29189 | Central | DKW | [7 empty] | TARM VARMEVÆRK | 0.4433% | 65.5 | 35.5 | 65.5 | 35.5 | 31.8935 |  |  | 204
205 | KERTEMINDE FORSYNING - VARME A/S | 29189 | Decentral | DKW | [7 empty] | THISTED VARMEFORSYNING A.M.B.A. |  | 68 | 42 | 73 | 39 |  | 14.82% | 166.447 | 205
206 | KIBÆK VARMEVÆRK ADMINISTRATIONSKONTORET | 29189 | Decentral | DKW | 0% | 65 | 33 | 65 | 34 |  | 26.87% | THORSHØJ KRAFTVARMEVÆRK | 1.721% | 70 | 45 | 75 | 40 | 35.5465 | 43.96% | 1.6 | 206
207 | KJELLERUP FJERNVARME AMBA | 29189 | Decentral | DKW | 0% | 68 | 31 | 70 | 32 | 36.0019 | 18.42% | THORSMINDE VARMEVÆRK A.M.B.A. |  | 67 | 40 | 80 | 40 |  |  |  | 207
208 | KLEJTRUP VARMEVÆRK | 29189 | Decentral | DKW | [7 empty] | THYBORØN FJERNVARME A.M.B.A. |  | 73 | 38 | 75 | 40 | 34.2076 | 32.76% | 18.1435 | 208
209 | Klinkby Kraftvarme A.m.b.A. | 29189 | Decentral | DKW | [7 empty] | TIM KRAFTVARMEVÆRK |  | 73 | 34 | 73 | 34 |  | 20.88% | 8.004 | 209
210 | Klitmøller | 29189 | Decentral | DKW | [7 empty] | TOFTLUND FJERNVARME A.M.B.A. | 12.1% | 73 | 39 | 70 | 38 | 32.4237 | 20.63% | 17.774 | 210
211 | KLOKKERHOLM FJERNVARME | 29189 | Decentral | DKW | [7 empty] | TOMMERUP BYS FJERNVARMEF. A.M.B.A. |  | 61 | 36 | 67 | 34 | 46.7552 | 11.63% | 18.766 | 211
212 | Kloster Kraftvarmeværk | 29189 | Decentral | DKW | [7 empty] | TRANBJERG VARMEVÆRK A.M.B.A. |  | 72 | 33 | 75 | 0 |  |  |  | 212
213 | Kolind Fjernvarmeværk A/S | 29189 | Decentral | DKW | [7 empty] | TRANUM KRAFTVARMEVÆRK |  | 74 | 38 | 75 | 34 |  | 33.36% | 3.188 | 213
214 | KONGERSLEV FJERNVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 70 | 40 | 75 | 35 |  | 22.8% | TRE-FOR VARME A/S |  | 68 | 45 | 82 | 43 |  | 23.97% | 647.531 | 214
215 | KVÆRNDRUP FJERNVARMECENTRAL A M B A | 29188 | Decentral | DKW | 0% | 65 | 35 | 80 | 32 | 0 | 31.73% | TRUSTRUP-LYNGBY VARMEVÆRK |  | 72 | 0 | 76 | 0 |  |  |  | 215
216 | KØGE VARME A/S | 29189 | Decentral | DKE | [7 empty] | TVERSTED KRAFTVARMEVÆRK | 0.5388% | 70 | 35 | 72 | 35 | 33.3246 | 35.75% | 4.388 | 216
217 | KØLVRÅ FJERNVARMECENTRAL | 29189 | Decentral | DKW | [7 empty] | TVIS |  | 98 | 46 | 100 | 43 |  |  |  | 217
218 | LADING - FAJSTRUP VARMEFORSYNINGS-SELSKAB | 29189 | Decentral | DKW | [7 empty] | TØNDER FJERNVARMESELSKAB A.M.B.A. |  | 72 | 39 | 73 | 38 | 36.1478 | 22.65% | 60.081 | 218
219 | LANGAA VARMEVÆRK AMBA | 29189 | Decentral | DKW | 27.49% | 73 | 36 | 75 | 38 | 35.0471 | 27.31% | TØRRING KRAFTVARMEVÆRK |  | 69 | 39 | 74 | 34 |  | 31.35% | 16.681 | 219
220 | Laurbjerg Kraftvarmeværk | 29189 | Decentral | DKW | 0% | 72 | 42 | 74 | 37 | 32.7679 | 32.58% | TÅRNBYFORSYNING VARME A/S |  | 80 | 52 | 98 | 56 | 35.229 | 4.489% | 164.836 | 220
221 | LEM VARMEVÆRK | 29189 | Decentral | DKW | 2.112% | 80 | 40 | 80 | 40 | 51.6168 | 11.33% | TAARS VARMEVÆRK A.M.B.A. | 8.551% | 68 | 44 | 74 | 34 |  | 23.15% | 13.791 | 221
222 | LEMVIG VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 66 | 37.5 | 75 | 36 | 28.2339 | 18.27% | ULDUM VARMEVÆRK A.M.B.A. |  | 75 | 0 | 78 | 0 |  |  |  | 222
223 | LENDUM KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | [7 empty] | ULFBORG FJERNVARME A.M.B.A. |  | 71 | 38 | 71.7 | 35 | 59.152 | 23.42% | 17.401 | 223
224 | LOHALS VARMEFORSYNING A.M.B.A. | 29188 | Decentral | DKW | [7 empty] | ULSTED VARMEVÆRK A.M.B.A. |  | 70 | 38 | 78 | 34 |  | 22.57% | 8.29 | 224
225 | LOLLAND VARME A/S | 29188 | Decentral | DKE | [7 empty] | V. HJERMITSLEV VARMEVÆRK |  | 80 | 45 | 80 | 45 |  | 38.39% | 2.651 | 225
226 | LYSTRUP FJERNVARME A M B A | 55133 | Central | DKW | 0% | 65 | 43 | 68 | 36 | 28.5629 | 25.22% | VALLENSBÆK FJERNVARMEVÆRK A.M.B.A. |  | 70 | 40 | 80 | 40 |  | 21.69% | 17.4384 | 226
227 | LÆSØ VARME A/S | 45973 | Decentral | DKW | [7 empty] | VAMDRUP FJERNVARME A.M.B.A. |  | 76 | 39 | 78 | 36 | 52.4576 | 21.45% | 25.513 | 227
228 | LØGSTRUP VARMEVÆRK A M B A | 29189 | Decentral | DKW | 2.451% | 70 | 36 | 75 | 33 | 35.4195 | 27.39% | VEDDUM SKELUND VISBORG KRAFTVARMEVÆRK | 0.8637% | 71 | 37 | 76 | 36 |  | 47.15% | 5.702 | 228
229 | LØGSTØR FJERNVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 75 | 43 | 80 | 40 |  | 26.87% | VEJEN VARMEVÆRK A.M.B.A. |  | 80 | 40 | 80 | 40 | 35 | 19.61% | 78.819 | 229
230 | LØGTEN-SKØDSTR FJERNVARMEV A M B A | 55133 | Central | DKW | [7 empty] | VEJLBY FJERNVARMECENTRAL |  | 63 | 48 | 72 | 42 |  |  |  | 230
231 | LØJT KIRKEBY FJERNVARMESELSKAB AMBA | 29189 | Decentral | DKW | [7 empty] | VEJLE FJERNVARME A.M.B.A. |  | 78 | 51 | 85 | 42 |  | 15.95% | 158.447 | 231
232 | Løkken Varmeværk | 29189 | Decentral | DKW | 0% | 70 | 42 | 72 | 35 | 31.903 | 24.15% | VEMB VARMEVÆRK A.M.B.A. |  | 68 | 0 | 75 | 0 |  |  |  | 232
233 | Løkkensvejens Kraftvarmeværk Amba | 29189 | Decentral | DKW | [7 empty] | VERDO VARME A/S |  | 75 | 45 | 78 | 41 | 36.0221 | 23.53% | 399.696 | 233
234 | LØNSTRUP VARMEFORSYNING AMBA | 29189 | Decentral | DKW | 0% | 68 | 44 | 70 | 39 | 27.0766 | 49.92% | VESTEGNENS KRAFTVARMESELSKAB I/S |  | 100 | 50 | 115 | 50 |  | 2.461% | 2094.781 | 234
235 | Lørslev Fjernvarmeforsyning Amba | 29189 | Decentral | DKW | [7 empty] | VESTERVIG FJERNVARME A.M.B.A. | 2.999% | 66 | 35 | 66 | 33 |  | 18.79% | 11.2137 | 235
236 | Løsning Fjernvarme A m b a | 29189 | Decentral | DKW | 0% | 66 | 37 | 65 | 35 |  | 22.1% | VESTFORBRÆNDING I/S |  | 125 | 63 | 125 | 60 |  | 5.017% | 1152.974 | 236
237 | MALLING VARMEVÆRK AMBA | 55133 | Central | DKW | 0% | 60.38 | 38 | 68 | 35 |  | 17.37% | VESTFORSYNING VARME A/S | 0.2294% | 67 | 41 | 78 | 38 | 36.0303 | 23.96% | 274.492 | 237
238 | Manna-Thise Kraftvarmeværk | 29189 | Decentral | DKW | [7 empty] | VIBORG FJERNVARME |  | 66.8 | 41.3 | 68.5 | 39.2 | 28.1579 | 23.08% | 196.647 | 238
239 | MARIAGER FJERNVARME A M B A | 29189 | Decentral | DKW | [7 empty] | VIDEBÆK VARME A/S | 3.495% | 71 | 37 | 77 | 32 |  | 24.87% | 28.314 | 239
240 | MARSTAL FJERNVARME A M B A | 28856 | Decentral | DKW | 20.41% | 70 | 42 | 72 | 35 | 27.8131 | 24.18% | VINDERUP VARMEVÆRK A.M.B.A. | 0.836% | 65 | 35 | 72 | 34 | 42.2438 | 24.85% | 25.8974 | 240
241 | Mejlby Kraftvarmeværk | 29189 | Decentral | DKW | [7 empty] | VOERSÅ KRAFTVARMEVÆRK A.M.B.A. |  | 68 | 0 | 74 | 0 |  | 31.99% | 3.18 | 241
242 | Mellerup Kraftvarme A.M.B.A. | 29189 | Decentral | DKW | [7 empty] | VOJENS FJERNVARME A.M.B.A. |  | 76 | 42 | 76 | 39 | 38.7561 | 25.67% | 39.3742 | 242
243 | MELØSE - ST. LYNGBY ENERGISELSKAB A.M.B.A | 29189 | Decentral | DKE | [7 empty] | VORUPØR KRAFTVARMEVÆRK |  | 67 | 42 | 70 | 37 |  | 40.07% | 4.6526 | 243
244 | Middelfart Fjernvarme a.m.b.a. | 29189 | Central | DKW | 0% | 64 | 45 | 65 | 40 |  | 19.59% | VÆRLØSE VARMEVÆRK A.M.B.A. |  | 68 | 45 | 70 | 43 |  | 17.58% | 40.391 | 244
245 | Midtlangeland Fjernvarme | 29188 | Decentral | DKW | 0% | 73 | 0 | 73 | 0 |  | 22.8% | VÆRUM - ØRUM KRAFTVARMEVÆRK |  | 73 | 40 | 74 | 38 | 33.2933 | 48.75% | 2.8091 | 245
246 | MORSØ VARME A/S | 41333 | Decentral | DKW | [7 empty] | ÆRØSKØBING FJERNVARME A.M.B.A. |  | 74 | 39 | 76 | 34 |  | 25.55% | 10.597 | 246
247 | Mosede Fjernvarmeværk A.M.B.A | 44023 | Central | DKE | 0% | 73 | 0 | 73 | 0 | 28.5502 | 26.23% | ØLGOD FJERNVARMESELSKAB | 0.3443% | 66 | 39 | 70 | 36 | 31.1967 | 21.27% | 29.853 | 247
248 | MOU KRAFTVARME AMBA | 29189 | Decentral | DKW | [7 empty] | ØRUM VARMEVÆRK |  | 67 | 37 | 70 | 34 | 32.7458 | 26.69% | 9.42 | 248
249 | Møldrup Varmeværk | 29189 | Decentral | DKW | 7.394% | 70 | 34.5 | 72 | 33 | 33.6022 | 21.69% | ØSTBIRK VARMEVÆRK A.M.B.A. | 0.006973% | 72 | 39 | 76 | 34 | 34.87 | 26.73% | 10.507 | 249
250 | MØRKE FJERNVARMESELSKAB A M B A | 29189 | Decentral | DKW | 0% | 72 | 40 | 72 | 40 |  | 28.04% | ØSTER HORNUM VARMEVÆRK A.M.B.A. |  | 66 | 38 | 73 | 36 | 30.2011 | 31.53% | 6.3046 | 250
251 | MØRKØV VARMEVÆRK AMBA | 29189 | Decentral | DKE | 0.9431% | 67 | 42 | 81 | 34 | 32.4152 | 33.05% | ØSTER HURUP KRAFTVARMEVÆRK A.M.B.A. | 1.381% | 72 | 41 | 73 | 39 |  | 45.53% | 4.008 | 251
252 | NFS VARME A/S | 29189 | Central | DKW | [7 empty] | ØSTER TOREBY VARMEVÆRK | 1.676% | 70 | 0 | 80 | 0 |  | 30.54% | 31.953 | 252
253 | NFS VARME A/S | 29189 | Decentral | DKW | [7 empty] | ØSTERVRAA VARMEVÆRK |  | 70 | 35 | 75 | 32 | 39.6198 | 22.87% | 11.454 | 253
254 | NIBE VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 71 | 0 | 79 | 0 |  | 22.8% | AABENRAA-RØDEKRO FJERNVARME A.M.B.A. |  | 73 | 42 | 75 | 40 |  | 26.01% | 204.236 | 254
255 | Nimtofte og Omegns Fjernvarmeforsyning | 29189 | Decentral | DKW | 0% | 70 | 41 | 70 | 41 |  | 31.76% | AALBORG KOMMUNE |  | 75 | 40 | 82 | 39 | 42.5547 | 16.51% | 73.993 | 255
256 | NORDBY FJERNVARME A M B A | 31210 | Central | DKW | 0% | 60 | 0 | 80 | 0 |  | 17.37% | AARS FJERNVARMEFORSYNING |  | 78 | 40 | 82 | 35 |  | 25.64% | 95.868 | 256
257 | NR ALSLEV FJERNVARMEVÆRK A M B A | 29188 | Decentral | DKE | 0% | 75 | 52 | 80 | 45 |  | 25.36%
258 | Nr. Nissum Kraftvarme A.m.b.A. | 29189 | Decentral | DKW
259 | NRGI LOKALVARME A/S | 23795 | Decentral | DKW
260 | NRGI LOKALVARME A/S | 29189 | Decentral | DKW
261 | NYKØBING M FJERNVARMEVÆRK A M B A | 41333 | Decentral | DKW | 0% | 74 | 40 | 74 | 38 | 36.8441 | 21.89%
262 | NYKØBING SJ VARMEVÆRK | 29188 | Decentral | DKE | 0% | 73 | 41 | 75 | 40 | 3.552 | 27.66%
263 | NYSTED VARMEVÆRK A.M.B.A | 29188 | Decentral | DKE | 0% | 67 | 67 | 71 | 71 | 33.0303 | 26.49%
264 | NÆSTVED VARMEVÆRK | 29189 | Decentral | DKE | 0% | 75 | 53 | 85 | 47 | 34.1182 | 19.08%
265 | NØRAGER VARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW
266 | NØRRE-BROBY VARMEVÆRK | 29188 | Decentral | DKW
267 | NØRRE NEBEL FJERNVARME | 29189 | Decentral | DKW
268 | NØRRE SNEDE VARMEVÆRK | 29189 | Decentral | DKW | 0.724% | 72 | 38 | 76 | 35 | 34.727 | 15.66%
269 | Nørre Vorupør | 29189 | Decentral | DKW | 0% | 67 | 42 | 70 | 37 |  | 40.07%
270 | NØRRE AABY KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 68 | 40 | 70 | 37 |  | 23.82%
271 | NØRRESUNDBY FJERNVARMEFORS AMBA | 29189 | Central | DKW | 1.676% | 70 | 0 | 80 | 0 |  | 30.54%
272 | Odder Forsyningsselskab I/S | 32264 | Central | DKW | 0% | 69.13 | 44.59 | 73.07 | 39.2 | 0 | 24.21%
273 | Odsherred Varme A/S | 29188 | Decentral | DKE
274 | ONSBJERG VARMEVÆRK ApS | 23795 | Decentral | DKW
275 | OUE KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW
276 | OVERLUND FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 65 | 40 | 70 | 35 | 32.2096 | 24.17%
277 | OVTRUP VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 70 | 40 | 74 | 36 | 30.2175 | 24.84%
278 | PADBORG FJERNVARME A.M.B.A. POSTBOKS 193 | 29189 | Decentral | DKW | 0% | 70 | 40 | 77 | 36 | 0 | 24.6%
279 | PINDSTRUP VARMEVÆRK A M B A | 29189 | Central | DKW | 0% | 75 | 38 | 84 | 40 |  | 30.19%
280 | PRÆSTBRO KRAFTVARMEVÆRK A M B A | 29189 | Decentral | DKW
281 | PRÆSTØ FJERNVARME | 29189 | Decentral | DKE | 0% | 75 | 0 | 80 | 0 |  | 23.11%
282 | RAMME VARMEVÆRK | 29189 | Decentral | DKW
283 | RAMSING LEM LIHME KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 74 | 42 | 77 | 40 | 29.494 | 47.07%
284 | Rask Mølle Varmeværk | 29189 | Decentral | DKW | 0% | 69 | 69 | 75 | 75 |  | 22.8%
285 | Ravnkilde Kraftvarmeværk A M B A | 29189 | Decentral | DKW
286 | Refa, Horbelev Fjernvarme a/s | 29188 | Decentral | DKE
287 | Refa, Kettinge Forsyning aps | 29188 | Decentral | DKE
288 | REFA, STUBBEKØBING FJERNVARME A/S | 29188 | Decentral | DKE
289 | RINGE FJERNVARMESELSKAB A M B A POSTBOKS 140 | 29188 | Decentral | DKW | 0% | 69 | 42 | 79 | 40 | 31.9222 | 25.57%
290 | RINGKØBING FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKW | 0.6503% | 67 | 39 | 67 | 35 |  | 25.36%
291 | RINGSTED FJERNVARME A/S | 18957 | Decentral | DKE | 0% | 75 | 45 | 85 | 48 | 0 | 18.81%
292 | Rise Fjernvarme A.M.B.A. | 28856 | Decentral | DKW | 0% | 84 | 40 | 82 | 36 |  | 34.89%
293 | ROSKILDE VARME A/S | 29189 | Central | DKE | 0% | 76 | 48 | 77 | 46 | 30.8916 | 19.9%
294 | Roslev Fjernvarmeselskab A.m.b.A. | 29189 | Decentral | DKW
295 | ROSTRUP KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW
296 | RY VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 66 | 0 | 72 | 0 |  | 22.41%
297 | RYE KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | 0% | 70 | 38 | 75 | 38 |  | 31.83%
298 | RYOMGAARD FJERNVARMEVÆRK | 29189 | Decentral | DKW | 0% | 70 | 40 | 70 | 40 |  | 27.65%
299 | RÆHR FJERNVARME AMBA | 29189 | Decentral | DKW | 0% | 68 | 43 | 72 | 39 |  | 41.13%
300 | Rødby Varmeværk A M B A | 29188 | Decentral | DKE | 4.146% | 75 | 52 | 80 | 45 | 33.0377 | 28.15%
301 | RØDBYHAVN FJERNVARME A M B A | 29188 | Decentral | DKE | 0% | 78 | 49 | 86 | 46 | 28.5627 | 23.78%
302 | RØDDING VARMECENTRAL | 29189 | Decentral | DKW | 0% | 77 | 39 | 77 | 39 | 37.8629 | 4.774%
303 | RØDKÆRSBRO FJERNVARMEVÆRK | 29189 | Decentral | DKW | 0% | 65 | 41 | 75 | 32 |  | 25.47%
304 | Rødovre Kommune | 65307 | Central | DKE | 0% | 70.2 | 47.3 | 75.9 | 46.7 | 26.8037 | 7.08%
305 | RØNDE FJERNVARMEVÆRK | 29189 | Central | DKW
306 | RØNNE VARME A/S | 26696 | Central | DKE
307 | SAKSKØBING FJERNVARMESELSKAB A M B A | 29188 | Decentral | DKE | 0% | 73 | 46 | 78 | 46 |  | 27.86%
308 | SALTUM FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 72 | 35 | 75 | 35 | 33.5117 | 22.92%
309 | SANDVED-TORNEMARK KRAFTVARMEVÆRK | 29189 | Decentral | DKE
310 | Sdr. Herreds Kraftvarmeværk A.m.b.a. | 41333 | Decentral | DKW
311 | Sdr. Nissum Fjernvarme I/S Henry Toft/Britha Pilgaard Toft | 29189 | Decentral | DKW
312 | Sdr. Omme Varmeværk Amba | 29189 | Decentral | DKW | 3.628% | 65 | 40 | 68 | 34 | 32.3104 | 25.45%
313 | SEAS-NVE KV-NET A/S | 29188 | Decentral | DKE
314 | SEAS-NVE KV-NET A/S | 29189 | Decentral | DKE
315 | SIG VARMEVÆRK | 29189 | Decentral | DKW | 0% | 68 | 36 | 70 | 33 | 0 | 26.02%
316 | SILKEBORG FORSYNING ERHVERV A/S | 29189 | Decentral | DKW | 0% | 66.1 | 44 | 69 | 39.5 | 27.7899 | 17.67%
317 | SINDAL VARMEFORSYNING A M B A | 29189 | Decentral | DKW | 0.3333% | 68 | 34 | 68 | 32 | 37.0409 | 25.27%
318 | SK VARME A/S | 29188 | Decentral | DKE
319 | SKAGEN VARMEVÆRK AMBA | 29189 | Decentral | DKW | 1.269% | 67 | 46 | 83 | 41 | 29.1114 | 30.55%
320 | SKALS KRAFTVARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | 0% | 70 | 38 | 74 | 34 | 37.8922 | 28.47%
321 | SKANDERBORG FJERNVARMECENTRAL | 29189 | Central | DKW
322 | SKANDERBORG FJERNVARMECENTRAL | 29189 | Decentral | DKW | 0% | 65 | 39 | 75 | 37 |  | 22.54%
323 | SKJERN FJERNVARMECENTRAL | 29189 | Decentral | DKW | 0% | 72 | 37 | 68 | 33 | 34.041 | 22.78%
324 | SKOVLUND VARMEVÆRK | 29189 | Decentral | DKW | 0% | 63 | 38 | 70 | 36 | 0 | 22.8%
325 | SKOVSGAARD VARMEVÆRK | 29189 | Decentral | DKW
326 | Skørping Varmeværk | 29189 | Decentral | DKW | 0% | 80 | 37 | 89 | 36 |  | 25.27%
327 | SKÅRUP FJERNVARME | 29189 | Decentral | DKW
328 | SMØRUM KRAFTVARME AMBA | 29188 | Decentral | DKE | 1.93% | 70 | 47 | 82 | 44 | 35.799 | 28.03%
329 | SNEDSTED VARMEVÆRK | 29189 | Decentral | DKW
330 | Snertinge, Særslev, Føllenslev Energiselskab A.M.B.A. | 29189 | Decentral | DKE
331 | SOLRØD FJERNVARMEVÆRK A M B A | 68534 | Decentral | DKE | 0% | 68 | 45 | 73 | 41 | 31.8647 | 22.92%
332 | SPJALD FJERNVARME- OG VANDVÆRK | 29189 | Decentral | DKW | 0.7828% | 65 | 39 | 65 | 32 | 30.5092 | 28.25%
333 | SPØTTRUP FJERNVARMEVÆRK | 29189 | Decentral | DKW
334 | ST. MERLØSE VARME A/S | 29189 | Decentral | DKE
335 | STEGE FJERNVARME AMBA POSTBOX 76 | 29189 | Decentral | DKE
336 | STENSTRUP FJERNVARME AMBA | 29189 | Decentral | DKW
337 | Stoholm Fjernvarmeværk | 29189 | Decentral | DKW
338 | STRANDBY VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 70 | 35 | 70 | 31 | 36.8101 | 24.73%
339 | STRUER FORSYNING FJERNVARME A/S | 29189 | Decentral | DKW | 0% | 68.5 | 41 | 72 | 35 | 38.3741 | 23.75%
340 | Støvring Kraftvarmeværk A.m.b.a. | 29189 | Decentral | DKW | 1.15% | 69 | 0 | 72 | 0 |  | 23.71%
341 | SVEBØLLE-VISKINGE FJERNVARMESELSKAB A.M.B.A. V/SVEND MYLLER | 29189 | Decentral | DKE | 0% | 72 | 41 | 88 | 39 | 0 | 22.8%
342 | Svendborg Fjernvarme A.m.b.a | 29189 | Decentral | DKW | 0% | 85 | 45 | 85 | 45 |  | 22.41%
343 | SVOGERSLEV FJERNVARMECENTRAL | 29189 | Central | DKE
344 | SYDFALSTER VARMEVÆRK A M B A | 29188 | Decentral | DKE | 2.678% | 71.2 | 44.4 | 76.7 | 37.6 | 46.5164 | 33.45%
345 | SYDLANGELAND FJERNVARME A.M.B.A. | 29188 | Decentral | DKW | 0% | 80 | 40 | 80 | 38 |  | 42.86%
346 | SÆBY VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 66 | 43 | 75 | 34 | 33.1896 | 27.48%
347 | Søndbjerg Fjernvarme Amba | 29189 | Decentral | DKW
348 | SØNDERBORG FJERNVARME AMBA | 29189 | Decentral | DKW | 0% | 79.43 | 46.72 | 80.96 | 41.73 |  | 24.48%
349 | SØNDERHOLM VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0.2082% | 71 | 39 | 75 | 39 |  | 31.18%
350 | TARM VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0.4433% | 65.5 | 35.5 | 65.5 | 35.5 | 31.8935 | 22.8%
351 | TERNDRUP FJERNVARME A M B A | 29189 | Decentral | DKW
352 | THISTED VARMEFORSYNING A M B A | 29189 | Decentral | DKW | 0% | 68 | 42 | 73 | 39 |  | 14.82%
353 | THORSAGER FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKW
354 | Thorshøj Kraftvarmeværk Amba | 29189 | Decentral | DKW | 1.721% | 70 | 45 | 75 | 40 | 35.5465 | 43.96%
355 | THORSMINDE VARMEVÆRK A.M.B.A. | 29189 | Decentral | DKW | 0% | 67 | 40 | 80 | 40 |  | 22.8%
356 | THORSØ FJERNVARMEVÆRK A M B A | 29189 | Decentral | DKW
357 | THYBORØN FJERNVARME A.M.B.A. | 29189 | Decentral | DKW | 0% | 73 | 38 | 75 | 40 | 34.2076 | 32.76%
358 | Tim Kraftvarmeværk | 29189 | Decentral | DKW | 0% | 73 | 34 | 73 | 34 |  | 20.88%
359 | TISTRUP VARMEVÆRK | 29189 | Decentral | DKW
360 | TOMMERUP BYS FJERNVARMEFORSYNING | 29189 | Decentral | DKW | 0% | 61 | 36 | 67 | 34 | 46.7552 | 11.63%
361 | TOMMERUP ST VARMEFORSYNING A M B A | 29189 | Decentral | DKW
362 | TRANBJERG VARMEVÆRK A M B A | 55133 | Central | DKW | 0% | 72 | 33 | 75 | 0 | 0 | 17.37%
363 | TRANUM VARMEVÆRK | 29189 | Decentral | DKW | 0% | 74 | 38 | 75 | 34 |  | 33.36%
364 | TRE-FOR VARME A/S | 29189 | Central | DKW | 0% | 68 | 45 | 82 | 43 |  | 23.97%
365 | TRE-FOR VARME A/S | 29189 | Decentral | DKW | 0% | 68 | 45 | 82 | 43 |  | 23.97%
366 | TRE-FOR VARME A/S | 69116 | Central | DKW | 0% | 68 | 45 | 82 | 43 |  | 23.97%
367 | TRE-FOR VARME A/S | 69116 | Decentral | DKW | 0% | 68 | 45 | 82 | 43 |  | 23.97%
368 | TROLDHEDE FJERNVARME | 29189 | Decentral | DKW
369 | TRUSTRUP-LYNGBY VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 72 | 0 | 76 | 0 |  | 22.8%
370 | Tversted Kraftvarmeværk A.M.B.A. | 29189 | Decentral | DKW | 0.5388% | 70 | 35 | 72 | 35 | 33.3246 | 35.75%
371 | TVIS TREKANTOMRÅDETS VARMETRANS MISSIONSSELSKAB I/S | 29189 | Central | DKW | 0% | 98 | 46 | 100 | 43 |  | 22.8%
372 | TVIS TREKANTOMRÅDETS VARMETRANS MISSIONSSELSKAB I/S | 29189 | Decentral | DKW | 0% | 98 | 46 | 100 | 43 |  | 22.8%
373 | Tørring Kraftvarmeværk | 29189 | Decentral | DKW | 0% | 69 | 39 | 74 | 34 |  | 31.35%
374 | TÅRNBYFORSYNING VARME A/S | 20310 | Central | DKE | 0% | 80 | 52 | 98 | 56 | 35.229 | 4.489%
375 | Tårs Varmeværk | 29189 | Decentral | DKW | 8.551% | 68 | 44 | 74 | 34 | 0 | 23.15%
376 | Uggelhuse-Langkastrup Kraftvarmeværk AMBA | 29189 | Decentral | DKW
377 | Ulbjerg Kraft/Varme A M B A | 29189 | Decentral | DKW
378 | Uldum Varmeværk Amba | 29189 | Decentral | DKW | 0% | 75 | 0 | 78 | 0 |  | 22.8%
379 | ULFBORG FJERNVARME | 29189 | Decentral | DKW | 0% | 71 | 38 | 71.7 | 35 | 59.152 | 23.42%
380 | ULSTED VARMEVÆRK | 29189 | Decentral | DKW | 0% | 70 | 38 | 78 | 34 |  | 22.57%
381 | ULSTRUP VARMEVÆRK A M B A | 29189 | Decentral | DKW
382 | V HJERMITSLEV VARMEVÆRK | 29189 | Decentral | DKW | 0% | 80 | 45 | 80 | 45 |  | 38.39%
383 | VALLENSBÆK FJERNVARMEVÆRK A M B A | 19583 | Central | DKE | 0% | 70 | 40 | 80 | 40 | 0 | 21.69%
384 | VAMDRUP FJERNVARME I M B A | 29189 | Decentral | DKW | 0% | 76 | 39 | 78 | 36 | 52.4576 | 21.45%
385 | VARDE VARMEFORSYNING A/S | 29189 | Central | DKW
386 | Varmeværket (pnr: 1003267160) | 19583 | Central | DKE
387 | Varmeværket (pnr: 1003267160) | 66137 | Central | DKE
388 | VEDDUM-SKELUND-VISBORG KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW | 0.8637% | 71 | 37 | 76 | 36 |  | 47.15%
389 | VEGGER VARMEVÆRK A M B A | 29189 | Decentral | DKW
390 | VEJBY-TISVILDE FJERNVARME AMBA | 29188 | Decentral | DKE
391 | VEJEN VARMEVÆRK | 29189 | Decentral | DKW | 0% | 80 | 40 | 80 | 40 | 35 | 19.61%
392 | VEJLBY FJERNVARMECENTRAL | 55133 | Central | DKW | 0% | 63 | 48 | 72 | 42 |  | 17.37%
393 | Vejle Fjernvarme A M B A | 29189 | Central | DKW | 0% | 78 | 51 | 85 | 42 |  | 15.95%
394 | VEJLEG FJERNVARMECEN V/LRS JENSEN | 19583 | Central | DKE
395 | VEJLEG FJERNVARMECEN V/LRS JENSEN | 19583 | Decentral | DKE
396 | VEMB VARMEVÆRK | 29189 | Decentral | DKW | 0% | 68 | 0 | 75 | 0 |  | 22.8%
397 | VERDO VARME A/S | 29189 | Central | DKW | 0% | 75 | 45 | 78 | 41 | 36.0221 | 23.53%
398 | VESLØS FJERNVARME AMBA | 29189 | Decentral | DKW
399 | VESTEGNENS KRAFTVARMESELSKAB I/S | 29189 | Decentral | DKE | 0% | 100 | 50 | 115 | 50 |  | 2.461%
400 | VESTEGNENS KRAFTVARMESELSKAB I/S | 44023 | Central | DKE | 0% | 100 | 50 | 115 | 50 |  | 2.461%
401 | VESTEGNENS KRAFTVARMESELSKAB I/S | 44023 | Decentral | DKE | 0% | 100 | 50 | 115 | 50 |  | 2.461%
402 | VESTERVIG FJERNVARME V/BRIAN LAURIDSEN | 29189 | Decentral | DKW | 2.999% | 66 | 35 | 66 | 33 |  | 18.79%
403 | VESTFORSYNING VARME A/S | 29189 | Decentral | DKW | 0.2294% | 67 | 41 | 78 | 38 | 36.0303 | 23.96%
404 | VIBORG FJERNVARME | 29189 | Decentral | DKW | 0% | 66.8 | 41.3 | 68.5 | 39.2 | 28.1579 | 23.08%
405 | VIDEBÆK VARME A/S | 29189 | Decentral | DKW | 3.495% | 71 | 37 | 77 | 32 |  | 24.87%
406 | Vildbjerg Varmeværk A.m.b.a. | 29189 | Decentral | DKW
407 | VINDERUP VARMEVÆRK A M B A | 29189 | Decentral | DKW | 0.836% | 65 | 35 | 72 | 34 | 42.2438 | 24.85%
408 | VISSENBJERG FJERNVARME AMBA | 29189 | Decentral | DKW
409 | VIVILD VARMEVÆRK A M B A | 29189 | Decentral | DKW
410 | VOERSÅ KRAFTVARMEVÆRK A M B A | 29189 | Decentral | DKW | 0% | 68 | 0 | 74 | 0 |  | 31.99%
411 | VOJENS FJERNVARME A.M.B.A. | 29189 | Decentral | DKW | 0% | 76 | 42 | 76 | 39 | 38.7561 | 25.67%
412 | VORDINGBORG FJERNVARME A/S | 29189 | Decentral | DKE
413 | VRÅ VARMEVÆRK AMBA | 29189 | Decentral | DKW
414 | VÆRLØSE VARMEVÆRK A M B A | 29188 | Decentral | DKE | 0% | 68 | 45 | 70 | 43 |  | 17.58%
415 | Værum-Ørum Kraftvarmeværk AMBA | 29189 | Decentral | DKW | 0% | 73 | 40 | 74 | 38 | 33.2933 | 48.75%
416 | YouSee A/S | 55133 | Central | DKW
417 | ÆRØSKØBING FJERNVARME | 28856 | Decentral | DKW | 0% | 74 | 39 | 76 | 34 |  | 25.55%
418 | Ø BRØNDERSLEV FJERNVARMEVÆRK | 29189 | Decentral | DKW
419 | Ø HORNUM VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 66 | 38 | 73 | 36 | 30.2011 | 31.53%
420 | ØLAND KRAFTVARMEVÆRK AMBA | 29189 | Decentral | DKW
421 | Ølgod Fjernvarmeselskab AMBA | 29189 | Decentral | DKW | 0.3443% | 66 | 39 | 70 | 36 | 31.1967 | 21.27%
422 | Ørnhøj-Grønbjerg Kraftvarme | 29189 | Decentral | DKW
423 | ØRSTED FJERNVARMEVÆRK | 29189 | Decentral | DKW
424 | ØRUM VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 67 | 37 | 70 | 34 | 32.7458 | 26.69%
425 | Østbirk Fjernvarmeværk A M B A. | 29189 | Decentral | DKW | 0.006973% | 72 | 39 | 76 | 34 | 34.87 | 26.73%
426 | Øster Hurup Kraftvarmeværk | 29189 | Decentral | DKW | 1.381% | 72 | 41 | 73 | 39 | 0 | 45.53%
427 | ØSTERILD FJERNVARMESELSKAB A M B A | 29189 | Decentral | DKW
428 | ØSTERVRÅ VARMEVÆRK AMBA | 29189 | Decentral | DKW | 0% | 70 | 35 | 75 | 32 | 39.6198 | 22.87%
429 | Aabenraa - Rødekro Fjernvarme Amba | 29189 | Central | DKW | 0% | 73 | 42 | 75 | 40 |  | 26.01%
430 | Aabenraa - Rødekro Fjernvarme Amba | 29189 | Decentral | DKW | 0% | 73 | 42 | 75 | 40 |  | 26.01%
431 | AABYBRO FJERNVARME | 29189 | Decentral | DKW
432 | Aadum Kraftvarmeværk | 29189 | Decentral | DKW
433 | Aalborg kommune | 29189 | Central | DKW | 0% | 75 | 40 | 82 | 39 | 42.5547 | 16.51%
434 | Aalborg kommune | 29189 | Decentral | DKW | 0% | 75 | 40 | 82 | 39 | 42.5547 | 16.51%
435 | Ålestrup Varme A M B A | 29189 | Decentral | DKW
436 | Århus Kommune | 55133 | Central | DKW | 0% | 75 | 46 | 81 | 42 | 27.491 | 21%
437 | Århus Kommune | 55133 | Decentral | DKW | 0% | 75 | 46 | 81 | 42 | 27.491 | 21%
438 | Aars Fjernvarmeforsyning Amba | 29189 | Decentral | DKW | 0% | 78 | 40 | 82 | 35 |  | 25.64%
256

## Demand_Proj
Trans - Insert
| TimeSlice | LimType | Attribute | Year | DKW | DKE | Cset_Set | Cset_CN |  | DEA's linear projection taken from 2026 (it will be probably present in COWI's report), while for the period 2017-2025 Energinet projection is kept:
| *Unit | [9 empty] | Total estimated power consumption [MWh] | Total IT estimated power consumption [MWh] | IT Installed power [MW] | Annual IT Power consumption - Central [GWh] | Annual IT Power consumption - Decentral [GWh] |  | Usage profile assumption coming from "RenewIT" project (deliverable 4.5) [http://www.renewit-project.eu/documents/deliverable/]
|  |  | COM_PROJ | 2017 | 0 | 0 | DEM | ELDCC |  | 2017 | 0 | 0 | 0 | 0 | 0 |  | Average daily load
|  |  | COM_PROJ | 2018 | 0 | 0 | DEM | ELDCC | 0 | 2018 | 0 | 0 | 0 | 0 | 0 |  | Hour | Load
|  |  | COM_PROJ | 2019 | 0.43128 | 0 | DEM | ELDCC | 0.22 | 2019 | 220000 | 200000 | 22.8311 | 119.7995 | 80.2005 | Cooling system power (% of IT load) | 1 | 53%
|  |  | COM_PROJ | 2020 | 1.7232 | 0 | DEM | ELDCC | 0.879 | 2020 | 879000 | 799090.9091 | 91.2204 | 478.6535 | 320.4375 | 10% | 2 | 50%
|  |  | COM_PROJ | 2021 | 3.4483 | 0 | DEM | ELDCC | 1.759 | 2021 | 1759000 | 1599090.9091 | 182.5446 | 957.8514 | 641.2395 |  | 3 | 49%
|  |  | COM_PROJ | 2022 | 5.1283 | 0 | DEM | ELDCC | 2.616 | 2022 | 2616000 | 2378181.8182 | 271.4819 | 1424.5249 | 953.6569 | Percentage of Decentral DC until 2025 | 4 | 49%
|  |  | COM_PROJ | 2023 | 6.6809 | 0 | DEM | ELDCC | 3.408 | 2023 | 3408000 | 3098181.8182 | 353.6737 | 1855.8031 | 1242.3787 | 40.1% | 5 | 49%
|  |  | COM_PROJ | 2024 | 8.059 | 0 | DEM | ELDCC | 4.111 | 2024 | 4111000 | 3737272.7273 | 426.6293 | 2238.617 | 1498.6557 |  | 6 | 53%
|  |  | COM_PROJ | 2025 | 9.2666 | 0 | DEM | ELDCC | 4.727 | 2025 | 4727000 | 4297272.7273 | 490.5562 | 2574.0556 | 1723.2171 |  | 7 | 58%
|  |  | COM_PROJ | 2026 | 17.1949 | 0 | DEM | ELDCC | 5.254 | 2026 | 5254000 | 4776363.6364 | 545.247 | 4776.3636 | 1723.2171 |  | 8 | 58%
|  |  | COM_PROJ | 2027 | 18.7069 | 0 | DEM | ELDCC | 5.716 | 2027 | 5716000 | 5196363.6364 | 593.1922 | 5196.3636 | 1723.2171 |  | 9 | 63%
|  |  | COM_PROJ | 2028 | 20.1469 | 0 | DEM | ELDCC | 6.156 | 2028 | 6156000 | 5596363.6364 | 638.8543 | 5596.3636 | 1723.2171 |  | 10 | 68%
|  |  | COM_PROJ | 2029 | 21.5836 | 0 | DEM | ELDCC | 6.595 | 2029 | 6595000 | 5995454.5455 | 684.4126 | 5995.4545 | 1723.2171 |  | 11 | 68%
|  |  | COM_PROJ | 2030 | 23.0236 | 0 | DEM | ELDCC | 7.035 | 2030 | 7035000 | 6395454.5455 | 730.0747 | 6395.4545 | 1723.2171 |  | 12 | 68%
|  |  | COM_PROJ | 2031 | 24.4636 | 0 | DEM | ELDCC | 7.475 | 2031 | 7475000 | 6795454.5455 | 775.7368 | 6795.4545 | 1723.2171 |  | 13 | 68%
|  |  | COM_PROJ | 2032 | 25.9004 | 0 | DEM | ELDCC | 7.914 | 2032 | 7914000 | 7194545.4545 | 821.2951 | 7194.5455 | 1723.2171 |  | 14 | 68%
|  |  | COM_PROJ | 2033 | 27.3371 | 0 | DEM | ELDCC | 8.353 | 2033 | 8353000 | 7593636.3636 | 866.8535 | 7593.6364 | 1723.2171 |  | 15 | 68%
|  |  | COM_PROJ | 2034 | 28.7738 | 0 | DEM | ELDCC | 8.792 | 2034 | 8792000 | 7992727.2727 | 912.4118 | 7992.7273 | 1723.2171 |  | 16 | 68%
|  |  | COM_PROJ | 2035 | 30.2105 | 0 | DEM | ELDCC | 9.231 | 2035 | 9231000 | 8391818.1818 | 957.9701 | 8391.8182 | 1723.2171 |  | 17 | 68%
|  |  | COM_PROJ | 2036 | 31.6473 | 0 | DEM | ELDCC | 9.67 | 2036 | 9670000 | 8790909.0909 | 1003.5284 | 8790.9091 | 1723.2171 |  | 18 | 68%
|  |  | COM_PROJ | 2037 | 33.084 | 0 | DEM | ELDCC | 10.109 | 2037 | 10109000 | 9190000 | 1049.0868 | 9190 | 1723.2171 |  | 19 | 68%
|  |  | COM_PROJ | 2038 | 34.5207 | 0 | DEM | ELDCC | 10.548 | 2038 | 10548000 | 9589090.9091 | 1094.6451 | 9589.0909 | 1723.2171 |  | 20 | 68%
|  |  | COM_PROJ | 2039 | 35.9575 | 0 | DEM | ELDCC | 10.987 | 2039 | 10987000 | 9988181.8182 | 1140.2034 | 9988.1818 | 1723.2171 |  | 21 | 68%
|  |  | COM_PROJ | 2040 | 37.3942 | 0 | DEM | ELDCC | 11.426 | 2040 | 11426000 | 10387272.7273 | 1185.7617 | 10387.2727 | 1723.2171 |  | 22 | 63%
[17 empty] | 23 | 58%
[17 empty] | 24 | 53%
| TimeSlice | LimType | Attribute | Year | DKW | DKE | Cset_Set | Cset_CN
*Unit
|  |  | COM_PROJ | 2017 | 0 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2018 | 0 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2019 | 0.28872 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2020 | 1.1536 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2021 | 2.3085 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2022 | 3.4332 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2023 | 4.4726 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2024 | 5.3952 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2025 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2026 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2027 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2028 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2029 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2030 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2031 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2032 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2033 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2034 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2035 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2036 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2037 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2038 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2039 | 6.2036 | 0 | DEM | ELDCD
|  |  | COM_PROJ | 2040 | 6.2036 | 0 | DEM | ELDCD
| TimeSlice | LimType | Attribute | Year | DKW | Pset_PN | Cset_CN
*Unit
|  |  | VDA_FLOP |  | 0.078954 | LDCF* | LDCCSELC
|  |  | VDA_FLOP |  | 0.58104 | LDCF* | LDCLTH*
Note on H2: Define the qualifiers based upon commodity set + name + descriptions, according to both include and exclude specifications.
Note on M3: Alessandro: Values of the projection comes from an anticipation of Steffen
Note on O4: Alessandro: Estimated power of IT components (servers, disks, ports) and power supply systems (UPSs, PDUs). This number includes everything that is not the cooling system
Note on P4: Alessandro: Energy projection comes from hypothesis that data centers work always at maximum power
Note on S7: Alessandro: Assumption based on EIA of Viborg data center (made by COWI) and confirmed by Google and Facebook environmental report
Note on S10: Alessandro: The only Large Data Center to be Decentral is Viborg, whose IT installed power is 160 MW when fully operative in 2025 (according to the EIA). Assumption that the data centers coming after 2025 will be in central location (Fredericia, Aabenraa...)
Note on H32: Define the qualifiers based upon commodity set + name + descriptions, according to both include and exclude specifications.
From RenewIT: this is the fraction of the installed IT power consumed by the servers (depending on the type of workload)
The "Web" profile was chosen. In RenewIT project only the servers are considered in the "IT power", so the profile was translated by an 8% up to account for power transmission lossess.
8% lossess estimated from paper: "Energy saving potential of various air-side economizers in a modular data center" - S. Ham et al.
(https://www.sciencedirect.com/science/article/pii/S0306261914011167)
From RenewIT: this is the fraction of the installed IT power consumed by the servers (depending on the type of workload)
The "Web" profile was chosen. In RenewIT project only the servers are considered in the "IT power", so the profile was translated by an 8% up to account for power transmission lossess.
8% lossess estimated from paper: "Energy saving potential of various air-side economizers in a modular data center" - S. Ham et al.
(https://www.sciencedirect.com/science/article/pii/S0306261914011167)